## Sheet1
Tottenham Hotspur Stadium (Plot 3, Section 73) GLA Comments
Flood risk, sustainable drainage, and water consumption
No. | Comment | Response
64 | London Plan Policy SI12 requires development proposals to ensure that flood risk is minimised and mitigated, and that residual risk is addressed. Policy SI13 states that development proposals should aim to achieve greenfield run-off rates and ensure that surface water run-off is managed as close to its source as possible, in line with the drainage hierarchy. Policy SI5 states that development proposals should minimise the use of mains water; incorporate measures to help achieve lower water consumption; ensure that adequate wastewater infrastructure capacity is provided; and minimise the potential for misconnections between foul and surface water | Surface water run-off is proposed to be managed as close to source as possible following the drainage hierarchy. SuDS are provided in the form of a geocellular attenutation tank restricting runoff up to the 1 in 100 year storm event + 40% climate change. There are no opportunities to incorporate green roofs on the hotel structure.
65 | The site is in Flood Zone 1, with a small area to the south-west being within Flood Zone 2, and is within a Critical Drainage Area. A Flood Risk Assessment (FRA) has been submitted. It should also be confirmed in the FRA that ground levels within Flood Zone 2 would remain as existing, and as such, will not displace fluvial floodwater off-site. Latest EA reservoir mapping shows that the southern extent of the site is at risk of reservoir flooding when river levels are normal. If the applicant can confirm the ground levels in Flood Zone 2 remain the same and that no sensitive receptors are proposed, a Flood Warning and Evacuation Plan (FWEP) should not be required. There is the potential for elevated groundwater beneath the site, and groundwater monitoring should be undertaken to inform the exact mitigation measures required, to be secured by condition. The level of risk to the site from sewers is unclear as this is not fully reviewed in the FRA. Further information should be provided, including the analysis of local sewer networks. The FRA provided for the proposed development does not yet comply with Policy SI12. | The ground levels within Flood Zone 2 are confirmed to be unchanged as this contains the existing road, pavement and a small part of public realm. It is therfore understood that there will be no displacement of fluvial floodwater off-site as a result of the proposal. The FFL for all More Vulnerable land uses are located above the area identified as being at risk of flooding from reservoirs when river levels are normal. The FRA specifies that the utilities located within the basement must ensure functioning of the building during an unlikley flooding event from reservoirs by incorporating flood resilient measures. No other sensitive receptors are identified. The overall risk of groundwater rising above ground level and causing flooding to the site is considered to be low. Part of the proposed basement has been constructed under a previous phase commencing in 2018. Two boreholes were installed in 2016 and a groundwater level of 12.79mbgl was observed. A standpipe monitoring levels between April and May 2016 did not encounter any groundwater and therefore risk from perched water is also considered low. No uplift or water ingress has been observed or recorded in the constructed basement to date. When construction is due to be undertaken to the basement extension, a monitoring plan will be put in place to ensure the flood risk remains low. There are no known issues associated with lack of capacity of the TW foul water sewer network. In addition, all surface water is proposed to be discharged to a dedicated surface water sewer. It is therefore considered that the risk of the TW foul sewer surcharging and flooding as a result of the proposed development is low. Thames Water have subsequently confirmed the following on 19th September: "If your proposals progress in line with the details you’ve provided, we’re pleased to confirm that there will be sufficient sewerage capacity in the adjacent foul water sewer network to serve your development." The risk of sewer water flooding to the development, in the event of surcharge such as through blockage, is also considered low due to the proposed development levels being higher than the existing road levels where the foul water and surface water sewers are located. Further details of the sewer location and sizing are provided in the Drainage Strategy.
66 | In terms of sustainable drainage, a greenfield runoff rate has been provided in Appendix E, the SuDS Proforma; however, this has not been referenced in the main body of the report and no consideration has been given to the practicality of discharging at greenfield rate. Discharge rates can be readily restricted to well below 5l/s. The drainage strategy assumes that infiltration is not feasible; however, there is a reasonable possibility that the site is suitable for infiltration. Soakage tests at various points should be undertaken to examine the feasibility of infiltration. | The planning application is for a S73 Minor material amendments to an existing application. Therefore the drainage strategy proposes to follow the previously agreed drainage strategy under the hybrid planning permission HGY/2015/3000. The original drainage strategy is based on an allowable discharge of 150l/s/ha totalling 1260l/s for the entire 8.4ha development site. For which Plot 3 has an allowance of 4.4l/s. The Plot 3 hotel area has increased from the previous proposal, however the strategy is to still restrict the discharge from this larger area to 4.4 l/s and provide attenuation for up to the 100 year storm event + 40% climate change. The podium area within the Plot 3 boundary decreases as a result of the increased hotel building footprint, this area is proposed to discharge to existing outfalls as it does currently. For the purposes of the drainage strategy, the worst case has been assumed (no infiltration) given the site's location and geology information suggesting that the ground conditions consist of london clay with low impermeability. Given the proposed location of the attenuation tank next to the hotel basement, infiltration at this location is not considered to be practical. BRE 365 guidelines suggest that soakaway should not be constructed within 5m of foundations for structures.
67 | The drainage strategy proposes below ground attenuation tanks. Rainwater harvesting and green roofs should also be provided to satisfy the requirements of Policy SI13. A conservative scenario has been adopted whereby no reuse of rainwater is assumed. The applicant should revise the drainage strategy to incorporate a range of SuDS to provide the required water quantity, quality, biodiversity, and amenity benefits. No calculations for the greenfield runoff rate are provided, which does not provide sufficient detail to support the proposed drainage strategy. Hydraulic calculations should be provided, including a range of return periods and storm durations, and included on the drainage drawings. An assessment of exceedance flood flow routes above the 100-year event plus 40% climate change is discussed; however, these should be presented and included on drainage strategy drawings. The surface water drainage strategy does not yet comply with Policy SI13 | SuDS provisions including geocellular attenuation tanks, and rainwater harvesting are present across the wider masterplan, it is not feasible to incorporate green roofs into the Plot 3 hotel scheme. As this is a S73 amendment to the original, compliance of policy should be assessed against the wider masterplan. Please also refer to the below comment regarding rainwater harvesting and reuse.
68 | In terms of water efficiency, no water efficiency information has been provided for the residential component. The Sustainability Statement notes that 3 Wat 01 credits are targeted for the non-residential uses on site, with water consumption reduced by 40%, in line with Policy SI5. Water efficient fittings, and leak detection systems are proposed, which is welcomed. The applicant should also include water harvesting and reuse to reduce consumption of water across the site. This can be integrated with the surface water drainage system to provide a dual benefit. The proposed development does not yet meet the requirements of Policy SI5. | For the residential component of the development, limiting flow rates on all water fittings have been imposed. The maximum flow rate figures proposed for the residential fittings are less than the requirements of the Approved Document Part G: Sanitation, hot water safety and water efficiency and are as per table below (Table 2-3 - Fitting flow rates and loading units, extract from Buro Happold Stage 2 MEP Report). The final figures however to be determined following the specification of sanitary wear by the interior designer. Rainwater harvesting and reuse - The incorporation of rainwater harvesting and reuse has been explored on the project previously. The potential areas for collecting rainwater throughout the development are limited and of relatively low surface area, resulting in relatively small water storage potential. Whilst it is appreciated the system could bring some benefits to the scheme, it is believed that the resulting embodied carbon associated with the equipment installation outways these benefits (storage tank, filtration system, pumps, all associated additional pipework runs etc.). For this reason, rainwater harvesting and reuse has not been pursued further.