## Witness
Project: | 808-812 Tottenham high road |  | Ref.:
System: | MEV 101 |  | Sheet: | 1 | of | 4
System Witness Certificate
The system detailed within has been witnessed to the Clients representative,
the test data is a true record of the system performance achieved
Witnessed By:
Company:
Date:
Test Completed By: |  | F. Di Bonito
Services Contractor: |  | Airflow services
Date: |  | 2026-01-12
Comments:
9-11 Wellesley Avenue, Richings Park, Iver, SL0 9AX - T: 01753 654934 - E: info@balcomm.co.uk - W: www.balcomm.co.uk

## Report (A)
Report Sheet
Project: | 808-812 Tottenham high road |  | Ref.:
System: | MEV 101 |  | Sheet: | 2 | of | 4
Report
I was instructed to attend site on behalf of Airflow Design to commission a Nuaire extract fan located on the first floor
W/C lobby. This Nuaire extract fan served 3 punkah louvres and was controlled via the use of a speed pot located internally
to the unit. This speed pot was set to 60%. Due to solid ceiling I was unable to obtain a correction factor therefore I applied
a standard factor of 1. All punkah louveres were balanced via the use of adjusting the punkah louvers until all were within
100-110% of design volume.
All readings were recorded.
Engineer: | F. Di Bonito |  | Date: | 2026-01-12
9-11 Wellesley Avenue, Richings Park, Iver, SL0 9AX - T: 01753 654934 - E: info@balcomm.co.uk - W: www.balcomm.co.uk

## Schemo (portrait)
System Schematic
Project: | 808-812 Tottenham high road | [6 empty] | Ref:
System: | MEV 101 | [6 empty] | Sheet: |  | 3 | of | 4
Extract discharge
EG 01
EG 03
EG 02
Engineer: |  | F. Di Bonito | [5 empty] | Date: | 2026-01-12
9-11 Wellesley Avenue, Richings Park, Iver, SL0 9AX - T: 01753 654934 - E: info@balcomm.co.uk - W: www.balcomm.co.uk
MEV 101

## Extract
Grille Balance Test Record
Project: | 808-812 Tottenham high road |  |  |  |  | Ref.:
System: | MEV 101 |  |  |  |  | Sheet: | 4 | of | 4
Design Information |  |  |  |  | Measured
Grille No. | Grille or Hood Size (mm) | Area m² | Design Volume m³/s | Design Velocity m/s | Final Velocity m/s | Measured Volume m³/s | Correction Factor | Actual Volume m³/s | Design %
Extract
EG 01 | 100 | 0.0078 | 0.008 | 1.03 | 1.1 | 0.009 | 1 | 0.009 | 107
EG 02 | 100 | 0.0078 | 0.008 | 1.03 | 1.1 | 0.009 | 1 | 0.009 | 107
EG 03 | 100 | 0.0078 | 0.015 | 1.92 | 2.1 | 0.016 | 1 | 0.016 | 109
The measuring hood correction factor is derived by dividing the duct | [6 empty] | Duct Total m³/s:
Pitot traverse volume by the total of the grille indicated volume | [6 empty] | Hood/Grille Total:
Correction Factor:
Comments:
Engineer: | F. Di Bonito |  |  |  |  | Date: | 2026-01-12
9-11 Wellesley Avenue, Richings Park, Iver, SL0 9AX - T: 01753 654934 - E: info@balcomm.co.uk - W: www.balcomm.co.uk
Note on J39: Enter Duct Total