## Witness
Project: | 808-812 Tottenham high road |  | Ref.:
System: | Basement server room extract fan |  | Sheet: | 1 | of | 4
System Witness Certificate
The system detailed within has been witnessed to the Clients representative,
the test data is a true record of the system performance achieved
Witnessed By:
Company:
Date:
Test Completed By: |  | F. Di Bonito
Services Contractor: |  | Airflow services
Date: |  | 2026-01-13
Comments:
9-11 Wellesley Avenue, Richings Park, Iver, SL0 9AX - T: 01753 654934 - E: info@balcomm.co.uk - W: www.balcomm.co.uk

## Report (A)
Report Sheet
Project: | 808-812 Tottenham high road |  | Ref.:
System: | Basement server room extract fan |  | Sheet: | 2 | of | 4
Report
I was instructed to attend site on behalf of Airflow Designs to commission a single extract Vent axia fan extracting air via a
single punkah louvre from the server room located in the basement. The design volume was 0.020l/s and this was achieved
via the use of adjustment of the punkah louvre until design volume was achieved.
All readings were recorded.
Engineer: | F. Di Bonito |  | Date: | 2026-01-13
9-11 Wellesley Avenue, Richings Park, Iver, SL0 9AX - T: 01753 654934 - E: info@balcomm.co.uk - W: www.balcomm.co.uk

## Schemo (portrait)
System Schematic
Project: | 808-812 Tottenham high road |  |  |  |  | Ref:
System: | Basement server room extract fan |  |  |  |  | Sheet: |  | 3 | of | 4
EG 01
Discharge
Engineer: |  | F. Di Bonito |  |  |  | Date: | 2026-01-13
9-11 Wellesley Avenue, Richings Park, Iver, SL0 9AX - T: 01753 654934 - E: info@balcomm.co.uk - W: www.balcomm.co.uk
Vent axia

## Grille Supply
Grille Balance Test Record
Project: | 808-812 Tottenham high road |  |  |  |  | Ref.:
System: | Basement server room extract fan |  |  |  |  | Sheet: | 4 | of | 4
Design Information |  |  |  |  | Measured
Grille No. | Grille or Hood Size (mm) | Area m² | Design Volume m³/s | Design Velocity m/s | Final Velocity m/s | Measured Volume m³/s | Correction Factor | Actual Volume m³/s | Design %
Extract
EG 01 | 100 | 0.0078 | 0.02 | 2.56 | 2.7 | 0.021 | 1 | 0.021 | 105
The measuring hood correction factor is derived by dividing the duct | [6 empty] | Duct Total m³/s:
Pitot traverse volume by the total of the grille indicated volume | [6 empty] | Hood/Grille Total:
Correction Factor:
Comments:
Engineer: | F. Di Bonito |  |  |  |  | Date: | 2026-01-13
9-11 Wellesley Avenue, Richings Park, Iver, SL0 9AX - T: 01753 654934 - E: info@balcomm.co.uk - W: www.balcomm.co.uk
Note on J39: Enter Duct Total