## Witness
Project: | 808-812 Tottenham high road |  | Ref.:
System: | EF-GF-01 |  | Sheet: | 1 | of | 3
System Witness Certificate
The system detailed within has been witnessed to the Clients representative,
the test data is a true record of the system performance achieved
Witnessed By:
Company:
Date:
Test Completed By: |  | F. Di Bonito
Services Contractor: |  | Airflow services
Date: |  | 2026-01-08
Comments:
9-11 Wellesley Avenue, Richings Park, Iver, SL0 9AX - T: 01753 654934 - E: info@balcomm.co.uk - W: www.balcomm.co.uk

## Report (A)
Report Sheet
Project: | 808-812 Tottenham high road |  | Ref.:
System: | EF-GF-01 |  | Sheet: | 2 | of | 3
Report
I was instructed to attend site on behalf of Airflow design to commission a Vent Axia extract fan located on the ground floor
cafe. This single toilet extract fan was serving only one punkah Louvre and was balanced via means of adjusting the
punkah louvre until design volume was achieved. The design volume for this extract punkah was 0.008 L/s.
The total being achieved was 0.009 L/s which equates to 107%. Due to solid ceiling and limited access I was unable to
obtain a pitot traverse and a correction factor therefore I applied a standard factor of 1.
All readings were recorded.
Engineer: | F. Di Bonito |  | Date: | 2026-01-08
9-11 Wellesley Avenue, Richings Park, Iver, SL0 9AX - T: 01753 654934 - E: info@balcomm.co.uk - W: www.balcomm.co.uk

## Extract
Grille Balance Test Record
Project: | 808-812 Tottenham high road |  |  |  |  | Ref.:
System: | EF-GF-01 |  |  |  |  | Sheet: | 3 | of | 3
Design Information |  |  |  |  | Measured
Grille No. | Grille or Hood Size (mm) | Area m² | Design Volume m³/s | Design Velocity m/s | Final Velocity m/s | Measured Volume m³/s | Correction Factor | Actual Volume m³/s | Design %
Extract
EG 01 | 100 | 0.0078 | 0.008 | 1.03 | 1.1 | 0.009 | 1 | 0.009 | 107
The measuring hood correction factor is derived by dividing the duct | [6 empty] | Duct Total m³/s:
Pitot traverse volume by the total of the grille indicated volume | [6 empty] | Hood/Grille Total:
Correction Factor:
Comments:
Engineer: | F. Di Bonito |  |  |  |  | Date: | 2026-01-08
9-11 Wellesley Avenue, Richings Park, Iver, SL0 9AX - T: 01753 654934 - E: info@balcomm.co.uk - W: www.balcomm.co.uk
Note on J39: Enter Duct Total