|  |  | Our ref: HGY/2026/1292 Contact: Kwaku Bossman-Gyamera Date: 12/06/2026 |
| --- | --- | --- |
| Town and Country Act 1990 (As amended) |  |  |
| Location: | 22 Palace Road, Wood Green, London, N11 2PS |  |
| Proposal: | Variation of conditions 2, 7 and 13 attached to planning permission HGY/2025/0363. The amendments relate to design detail regarding external appearance (condition 2), the proposed energy strategy (condition 7) and the Considerate Constructors Scheme (condition 13). |  |

Carbon Management Response 12/06/2026

Documents submitted:

- 250821 - 22 Palace Road - Energy and Sustainability Assessment rev 5

Response

Consented scheme (ref: HGY/2025/0363)

| Residential (including new build and refurbished flats) |  |  |  |
| --- | --- | --- | --- |
|  | Total regulated emissions (Tonnes CO2 / year) | CO2 savings (Tonnes CO2 / year) | Percentage savings (%) |
| Part L 2021 baseline | 5.6 |  |  |
| Be Lean | 3.5 | 2.2 | 38.7% |
| Be Clean | 3.5 | 0.0 | 0% |
| Be Green | 1.9 | 1.6 | 27.6% |
| Cumulative savings |  | 3.7 | 66.3% |
| Carbon shortfall to offset (tCO2) | 1.9 |  |  |
| Carbon offset contribution | £95 x 30 years x 1.9 tCO2/year = £5,415 |  |  |

Current proposal (S73):

| Residential (including new build and refurbished flats) |  |  |  |
| --- | --- | --- | --- |
|  | Total regulated emissions (Tonnes CO2 / year) | CO2 savings (Tonnes CO2 / year) | Percentage savings (%) |
| Part L 2021 baseline | 5.6 |  |  |
| Be Lean | 4.9 | 0.8 | 14% |
| Be Clean | 4.9 | 0.0 | 0% |
| Be Green | 3.7 | 1.2 | 20.5% |
| Cumulative savings |  | 1.9 | 34.5% |
| Carbon shortfall to offset (tCO2) | 3.7 |  |  |
| Carbon offset contribution | £95 x 30 years x 3.7 tCO2/year = £10,545 |  |  |

Energy Strategy

The current proposed overall carbon reduction is 34.5%, this has significantly reduced from 66.3% of the consented scheme.

Actions:

- The energy performance of the current proposal has deteriorated significantly from the consented scheme. Applicant should explore ways to revise their current energy proposal to align with the consented scheme.

Be Lean

The Be Lean carbon reduction of the consented scheme has also reduced significantly to 14% from 38.7% of the consented scheme. The current proposed thermal performance of the building specifications has been worsened from the consented scheme as below:

|  | Consented scheme |  | Current proposal |  |
| --- | --- | --- | --- | --- |
|  | New build | Refurbishment | New build | Refurbishment |
| External wall U-value | 0.16 W/m2K | 0.16 W/m2K | 0.18 W/m2K | 0.18 W/m2K |
| Floor U-value | Not provided | 0.12 W/m2K | 0.13 W/m2K | 0.25 W/m2K |

Actions:

- The thermal performance of the current proposal building specifications have worsened from the consented scheme. The current proposed external wall U-value have not improved beyond the notional value. As a result the Be Lean carbon reduction has reduced significantly. Applicant should explore ways to align the current proposed building fabric thermal performance with the consented scheme.

Be Green

|  | Consented scheme |  | Current proposal |  |
| --- | --- | --- | --- | --- |
|  | New build | Refurbishment | New build | Refurbishment |
| Heating system | Electric storage heaters. An average SHD of 14.6 kWh/m2.a has been demonstrated | Electric storage heaters. An average SHD of 14.6 kWh/m2.a has been demonstrated | Individual ASHPs | Gas boilers |
| PV output | 6 kWp |  | 7 kWp |  |

Actions:

- This application is proposing a gas boiler system for the refurbished units. All applications should demonstrate how they maximise on-site carbon emission reductions. It is strongly encouraged to replace the gas boiler strategy with a heat pump strategy instead to ensure the proposed dwelling is future-proofed and will not have any on-site fossil fuel combustion. It would enable this development to align with expectations in mitigating the climate emergency.

- The proposal of ASHPs to the new build is supported, applicant should consider extending the system to the refurbished units.

Overheating

Applicant has not addressed our previous concerns on overheating for the consented scheme.

The application site is in close proximity to the railway lines, this potential acoustic constraint might inhibit occupants’ ability to open the windows to mitigate OH risk.

The SE facing front elevation is exposed and the large windows on top floor have no external shading, this presents a high overheating risk.

Actions:

- Applicant is strongly encouraged to explore to incorporate external shading to mitigation OH risk passively.

- Applicant should revise their OH strategy to address the potential acoustic issue.

Conclusion

We cannot support this application currently.

Further information needs to be provided to address our comments in relation to the Energy Strategy and Overheating Strategy.