## Introduction
London Borough of Haringey - District Heating Network Technical Specification - Supporting Checklist - Rev01
This checklist has been developed to ensure all necessary details and documents are provided by the Developer to Haringey Council, to meet the requirements of the HDEN Specification (doc. 700336876-SPC-003) and Haringey Council planning conditions.
As well as CP1 and the HDEN Specification, the Developer shall carry out the design and installation in accordance with all applicable standards and regulations including but not limited to the following: • British & European Standards • Building Regulations • Environmental Regulations • Heat Network (Metering and Billing) Regulations 2014 • Medium Combustion Plant Directive (MCPD) • Health and Safety Executive (HSE) Regulations • CDM Regulations (2015) • Requirements of the Public Health Officer. • Requirements of the Fire Brigade / Fire Officer • Local by-laws • Good practice guidelines & standards of the local DNO and other similar DNO networks. • ENA Engineering Recommendations • CIBSE Code of Practice 1 - CP1 2020 • BG 62/2015 Heat Interface Units • BG 6 Design Framework for Building Services (2018) Where specific standards are referenced within this document, the Developer shall refer to the current version and amendments of each standard.
It is essential that information is submitted in a time period that allows the Authority to review, discuss and approve the information submitted. The time at which the information should be submitted is outlined in the column heading.

## Checklist
Item | HDEN Specification Reference (doc. 700336876-SPC-003) | CIBSE CP1 Objective/ Section | S106 Reference (All - 4.13.3, 4.13.5, 4.12.1b) | Information required with planning application | Information required prior to commencement of the development It is essential that information is submitted in a time period that allows the Authority to review and approve the information submitted. It is expected that this will be circa 3 months prior to commencement. Late submission will not be accepted as a reason for designs being inflexible. | Information required prior to above ground/superstructure works | Information required prior to occupation | Developer Comments | LBH Comments | Status A - Approved with no comments B - Approved with comments C - Rejected
Customer Heat Load Assessment | 2.8 | 3.2 |  | Provide calculations outlining methodology for calculating site peak DHW & space heating demand (customer heat load assessment). | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Primary Pipework Route | 5.2 | 3.6 |  | Provide a layout showing pipe route from the centre of the external road (where HDEN is located) to the heating plantroom. | Following a survey of existing below ground services (C2/GPR/trial hole), provide a section (supported by 3D model) showing proposed primary pipework route coordination with existing services from HDEN connection to building entry point. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Temporary Boiler Plant Location & Area | 4.4.4 | 2.3 | 4.12.1e | Confirm the structural load bearing of the temporary boiler location is adequate for the temporary plant and identify the area/route available for a flue. | Structural load bearing calculations for the temporary plant location and a plan showing flue route. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Pipework to Temporary Boiler Plant Location | 4.4.4 | 2.3 |  | Confirm that a pipework route has been allowed for from the thermal substation plant room to the temporary boiler location. | Provide a layout identifying proposed pipework route from thermal substation plant room to temporary boiler location. Identify pipework size, material, insulation, and strategy for future connection (i.e isolation valves, controls). | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Primary pipework installation/ joinery methods expansion/stress reduction methods | 5.2 | 3.7 |  | Provide primary network pipework and insulation material/size/thickness. | Provide description/specification for pipework installation method. Describe pipework expansion methods if applicable. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Heating & DHW diversificaton calculation | 2.8 | 3.2 |  | Provide heating and hot water diversification calculations. Include domestic and non-domestic accommodation & area schedules. Example calculations in CP1 3.2. Please also refer to DS 439. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Network heat loss calculations | 2.6, 2.8, 2.9, 2.12 | 3.5, 3.9 |  | Provide heat loss assessment required to determine the heat loss from the network within the building. Heat loss to be calculated for each dwelling, commercial space and total network. Developer to outline the parameters used for heat loss calculations including ambient air temperatures. These are to be in line with Table 2-9 & Appendix C of the HDEN spec. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Building Entry Point Detail | 5.2.7, 5.2.8 | 3.7 |  | Identify area/location for building entry pit on a layout, including dimensions. | Following a survey of existing below ground services, provide a detail/section of the DH building entry pit. Include dimensions, isolation points, cable tray for DEN comms cable, coordination with existing services and detail of flushing/seals. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Plant maintenance & operation strategy - Thermal substation & Primary pipework | 2.5, 2.7, 4.4 | 3.1, 3.7, 6 | 4.12.1e | Confirm that access requirements for installation and maintenance of primary pipework and the thermal substation have been considered, including replacement routes and the health and safety of installers/operators. | Provide strategy summarising plant and pipework access requirements for installation and maintenance, and replacement routes and methods, considering health and safety of operators. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Control Strategy | 6.4, 6.8, 7.4, 9 | 3.4, 3.5, 3.8, 5.5 |  | Confirm that general operation of BMS has been considered, including location of control panel and control philosophy, and controls of the thermal substation and primary plant. Confirm that an extra BMS connectivity point is allowed for (for future thermal substation). | Detail general operation and specification of BMS, location of control panel and control philosophy, controls of the thermal substation and primary plant. Developer to show that an extra BMS connectivity point is allowed for (for future thermal substation), as well as a heat availability signal and a minimum of two alarms. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
LTHW/DHW Building and Network Layouts | 2.11, 2.12, 5.3.2 | 3.6, 3.7 |  | Provide RIBA 3 coordinated heating & hot water services layouts for primary and secondary networks, including risers and corridors. Show primary pipework spacing on layout drawings, with dimensions. | Update for any changes following RIBA 4/contractor design. Provide 3D model, if applicable. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
System Description | 2 | 3.2, 3.4, 3.9, 3.5 |  | Provide a description of primary, secondary and tertiary systems. System description to include a description of the heat mix. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Pumping Design | 3, 6.5.1, 6.5.2, | 3.4, 3.5 |  | N/A | Outline maximum and minimum flow rates, pumping controls strategy and number of pumps in line with HDEN spec. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Network operating pressures - Primary Networks | 2.7 | 3.3 |  | N/A | Provide minimum and maximum operating pressures of the primary network. Confirm that control valves are in line with the differential pressure rating in section 2.7.2 of the HDEN spec. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Network operating pressures - Secondary/Tertiary Networks | 2.7 | 3.3 |  | N/A | Provide minimum and maximum operating pressures of the secondary heat networks (incl. dwellings). Confirm that control valves are in line with the differential pressure rating in section 2.7.2 of the HDEN spec. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Plant efficiencies | 2.13 | 3.5, |  | Provide plant efficiencies (in line with Table 2-12 of the HDEN Spec). | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Primary/secondary and dwelling LTHW & DHW flow & return temperatures | 2.6.2 | 3.4, Table 6, 3.5, |  | Provide LTHW & DHW flow & return temperatures. Maximum temperatures outlined in HDEN Spec Section 2.6.2 | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
LTHW/DHW Plant Schematic (incl. Thermal Substation) | 2.11, 2.12 | 3.5, 3.6 |  | Provide RIBA 3 level of detail heating & hot water services schematic. Schematic to show the pipe size, fluid velocity, pressure loss, & flow rate for each section of pipe. Schematic to show future connection of heat network and hydraulic arrangement of plantroom, preferably as a 'before connection' and 'after connection' arrangement. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
LTHW/DHW Plant Layout (incl. Thermal Substation) | 2.12, 2.14, 2.15, 5.3.2, 6.2 | 3.4, 3.7 | 4.12.1e | Provide RIBA 3 level of detail heating & hot water services layouts, including outlining the area/room for future thermal substation plant. Confirm primary pipework spacing has been considered. Refer to Figure 6.1 in the HDEN spec. | Show primary pipework spacing on layout drawings, with dimensions. Show plant access and maintenance zones. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
LTHW/DHW Building and Network Schematic | 6.2, 6.3, 6.5 | 3.4 | 4.12.1e | RIBA 3 level of detail heating & hot water services layouts. Layout should identify where pipes are running (i.e. underground, in ceiling void), and show dimensions for risers, celing voids. | Update for any changes following RIBA 4/contractor design. Provide 3D model, if applicable. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Thermal substation technical specification | 6.2, 6.3, 2.6 | 3.3, 4.3, 5.3 |  | N/A | Provide technical specification of the thermal substation (either manufacturer's or designer spec). | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
HIU specification incl. schematic | 7, 2.6.6, 2.11.2 | 3.3, 3.4, 4.3, 5.3 |  | N/A | Specification should be in line with the requirements outlined in Section 7.1 of the HDEN specification document. Schematic should be in line with Figure 6-1 of the HDEN Spec. HIU location to be shown and HIU sizing strategy to be provided | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Pipework length | 2.11 | 3.6, 3.9 |  | N/A | Pipework lengths to be shown on network schematic and outline where expansion methods are required. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Pipework design life schedule | 2.5 | 3.1, 3.5 |  | N/A | Provide design life of primary and secondary pipework and pipework accessories. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Future expansion peak DHW & space heating demand | 2.8 | 3.2 |  | If applicable, calculations outlining methodology to arrive at future expansion peak DHW & space heating demand (customer heat load assessment), as well as peaks of each phase of the development. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Primary Plant Metering Strategy | 6.4, 6.8, 7.4, 9 | 3.4, 3.5, 3.8, 5.5 | 4.13.11, 4.13.12 | Confirm general operation and specification of heat meters has been considered, including location of heat meters. | Provide strategy that details general operation and specification of heat meters, location of heat meters & metering philosophy. To confirm that all meters shall be connected to an Mbus system that enables full transfer of data to ESCo. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Electrical connection for thermal substation | 6.7, 4.3 | 3.3.6 |  | Confirm that the provision of LV distribution panel, lighting and small power for plantroom, and electrical supply to meters has been considered. | Developer to show the provision of LV distribution panel, lighting and small power for plantroom, and electrical supply to meters. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Ventilation provision for thermal substation | 4, 6.35 | 3.10 |  | Confirm that ventilation has been considered for the thermal substation room. | Provide description of ventilation strategy for thermal substation room, and plant selection and parameters if mechanically ventilated. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Overheating Assessment | 2.1 | 3.9 |  | Provide overheating assessment, in line with HDEN Spec/CP1 best practice heat loss within the building of less than 10% of annual heat consumption. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Plant redundancy - Heat Pumps | 2.15, 3.1.1 | 3.5 |  | Outline plant redundancy. Plant redundancy to be in line with Table 2-13 of the HDEN Spec. | Update required if information has changed | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
HIU cupboard details | 2.11.2 | 3.3, 3.4 |  | N/A | Provide detail showing HIU cupboard location, ventilation, accessibility, isolation, and incoming pipework location. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Tertiary network temperature controls | 8.1.3 | 3.3, 3.4 |  | Confirm that design is in line with section 8.1.3 of the HDEN spec. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Pipework spacing - Secondary Network | 5.3.2 | 3.7 |  | Show pipework spacing with dimensions on layout drawings | Update for any changes following RIBA 4/contractor design. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Secondary pipework installation/ joinery methods expansion/stress reduction methods | 5.2, 5.2.4 | 3.7 |  | Identify secondary network pipework and insulation material/thickness. Secondary pipework should follow the specification for energy centre and primary network pipework wherever possible. | Provide description/specification for secondary pipework installation method. Describe pipework expansion methods if applicable. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Plant maintenance & operation strategy - Plant other than thermal substation | 2.5, 2.7 | 3.1, 3.7 |  | Confirm that you have sufficiently considered plant access requirements for installation and maintenance, and replacement routes at this stage, considering health and safety of operators. | Provide strategy summarising plant access requirements for installation and maintenance, and replacement routes and methods, considering health and safety of operators. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Plant Schedule | 2, 2.5, 6.2, 6.5 | 3 |  | Confirm that the design life for plant items is in line with HDEN Spec Section 2.5 and/or CIBSE Guide M (2014 & 2019 update). | Provide a list identifying major plant items, capacities, operating parameters. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Health & Safety Plan/ Designer's risk assessment | 2.4.1 | 3.1, 4.1 |  | N/A | Provide the Health & Safety plan for the development and the primary side of the network connection. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Water Treatment plant | 2.17, 6.5 | 3.7.22 |  | Confirm that water treatment plant is provided for the cold water system serving the heat network. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Cold Water System connection details | 6.6 | 3.4.13 |  | Confirm that a cold water connection is provided to the plantroom/thermal substation location. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Pressurisation & Expansion Equipment | 6.5.3 | 3.10 |  | Confirm that pressurisation and expansion equipment is provided for each secondary network. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Wider Metering Strategy (Customers) | 6.4, 6.8, 7.4, 9 | 3.4, 3.5, 3.8, 5.5 | 4.13.11, 4.13.12 | Confirm that the general operation of meters for billing purposes (i.e. individual dwellings, commercial units), and location of heat meters has been considered at this stage. | Detail general operation and specification of meters for billing purposes (i.e. individual dwellings, commercial units), location of heat meters & metering philosophy. Confirm that all meters shall be connected to an Mbus system that enables full transfer of data to ESCo. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Vibration control | 2.18 | 3.7, 3.10 |  | N/A | Provide a declaration that anti-vibration mounting, spring hangers and plant supports have been considered and designed where required. | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Dwelling isolation details | 5.4 | 3.3, 3.7 |  | N/A | Confirm that lockable isolation valves will be provided external to the dwelling i.e in a service/common area which cannot be accessed by resident (example drawing Figure 5-2 of HDEN spec). | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Commercial isolation details | 6.1.1 | 3.7 |  | N/A | Confirm that lockable isolation valves will be provided external to the commercial unit i.e in a service/common area which cannot be accessed by consumer (example drawing Figure 5-2 of HDEN spec). | Update required if information has changed. Any changes require notification and approval. | Update required if information has changed. Any changes require notification and approval.
Commissioning | 10 | 5 |  | N/A | N/A | Issue a commissioning plan is to the Haringey Planning authority or their nominated representative. The commissioning plan should include all plant items/systems listed in 10.3.1 of the HDEN specification. | All systems to be commissioned by a specialist commissioning contractor in accordance with the requirements of CIBSE CP1 2020 (Section 5). The developer is to issue a commissioning/testing programme to Haringey Planning Authority. prior to any tests taking place. Haringey Planning authority or their nominated representative may attend any of the testing relevant to the heating system and network (i.e. thermal substation tests and commissioning, heat loss tests, pumping tests)
Dwelling domestic hot water delivery time | 2.6.4 |  |  | N/A | N/A | Update required if information has changed. Any changes require notification and approval. | Developer to provide evidence of hot water delivery time test. Test to show delivery time is less than 45 seconds.
Actual heat loss test | 10.5 |  |  | N/A | N/A | Update required if information has changed. Any changes require notification and approval. | The developer is to test the actual measured network heat loss. Refer to methodology in 10.5 of the HDEN Spec.