|  |  | Our ref: HGY/2023/3404 Contact: Eunice Huang Date: 10/04/2024 |
| --- | --- | --- |
| Town and Country Act 1990 (As amended) |  |  |
| Location: | Channing School, Highgate Hill, Hornsey, London, N6 5HF |  |
| Proposal: | 3-storey extension to north-eastern elevation of Brunner House, roof extension to the south-western elevation of Brunner House, refurbishment and façade alterations along with associated landscaping alterations. |  |

Carbon Management Response 10/04/2024

In preparing this consultation response, we have reviewed:

- Energy Statement prepared by Method Consulting (dated November 2023)

- Thermal comfort prepared by Method Consulting (dated November 2023)

- Sustainability Statement prepared by Method Consulting (dated December 2023)

- Relevant supporting documents.

- Summary

The development achieves a reduction of 39% carbon dioxide emissions on site, which is supported in principle. Some clarifications must be provided with regard to the Energy Strategy. Appropriate planning conditions will be recommended once this information has been provided.

- Energy – Overall

Policy SP4 of the Local Plan Strategic Policies, requires all new development to be zero carbon (i.e. a 100% improvement beyond Part L (2021)). The London Plan (2021) further confirms this in Policy SI2.

The overall predicted reduction in CO2 emissions for the development shows an improvement of approximately 39% in carbon emissions with SAP10.2 carbon factors, from the Baseline development model (which is Part L 2021 compliant). This represents an annual saving of approximately 1.1 tonnes of CO2 from a baseline of 2.8 tCO2/year.

| Non-residential (SAP10.2 emission factors) |  |  |  |
| --- | --- | --- | --- |
|  | Total regulated emissions (Tonnes CO2 / year) | CO2 savings (Tonnes CO2 / year) | Percentage savings (%) |
| Part L 2021 baseline | 2.8 |  |  |
| Be Lean | 2.6 | 0.2 | 9% |
| Be Clean | 2.6 | 0.0 | 0% |
| Be Green | 1.7 | 0.8 | 30% |
| Cumulative savings |  | 1.1 | 39% |
| Carbon shortfall to offset (tCO2) | 1.7 |  |  |
| Carbon offset contribution | £95 x 30 years x 1.7 tCO2/year = £4,845 |  |  |

Action:

- Please amend the Baseline modelling with the correct heating system efficiency in line with the GLA Energy Assessment Guidance 2022 and resubmit the following: (refer to Be Lean action below for details)

  - Revised Energy statement.

  - the GLA’s Carbon Emission Reporting Spreadsheet.

  - BRUKL sheets for a representative selection of the development for the Baseline, Be Lean and Be Green scenarios.

- The refurbished part of the development must be modelled, and the summary should include site-wide carbon reduction tables along with refurbishment and new build separately. Please use the notional specification for existing building while modelling the baseline scenario. Please refer to the GLA energy assessment guidance 2022.

Energy Use Intensity / Space Heating Demand

Applications are required to report on the total Energy Use Intensity and Space Heating Demand, in line with the GLA Energy Assessment Guidance (June 2022). The Energy Strategy should follow the reporting template set out in Table 5 of the guidance, including what methodology has been used. EUI is a measure of the total energy consumed annually but should exclude on-site renewable energy generation and energy use from electric vehicle charging.

| Building type | EUI (kWh/m2/year) | Space Heating Demand (kWh/m2/year) | Methodology used |
| --- | --- | --- | --- |

Actions:

- What is the calculated Energy Use Intensity (excluding renewable energy)? How does this perform against GLA benchmarks, i.e. at 65 kWh/m2/year? Please submit the information in line with the GLA’s reporting template.

- What is the calculated space heating demand? How does this perform against the GLA benchmark of 15 kWh/m2/year? Please submit the information in line with the GLA’s reporting template.

Energy – Lean

The applicant has proposed a saving of 0.2 tCO2 in carbon emissions (9%) through improved energy efficiency standards in key elements of the build, based on SAP10.2 carbon factors. This goes against the Energy Hierarchy and requirement to take a fabric first approach in line with London Plan Policy SI2 and Local Plan Policy SP4. However, it is understood that it is challenging for non-residential developments to reach the minimum 15% requirement against Part L 2021. Therefore, the development is required to maximise improvement in building fabric parameters as much as possible.

The following u-values, g-values and air tightness are proposed:

| Floor u-value | 0.12 W/m2K |
| --- | --- |
| External wall u-value | 0.15 W/m2K |
| Roof u-value | 0.12 W/m2K |
| Door u-value | 1.40 W/m2K |
| Window u-value | 1.40 W/m2K |
| G-value | 0.40 |
| Air permeability rate | 3 m3/hm2 @ 50Pa |
| Ventilation strategy | Natural ventilation Mechanical ventilation with heat recovery |
| Thermal bridging | Accredited Construction Details |
| Low energy lighting | 100% high efficacy 140lm/W |

London Plan Policy SI4 requires developments to minimise adverse impacts on the urban heat island, reduce the potential for overheating and reduce reliance on air conditioning systems. Through careful design, layout, orientation, materials and incorporation of green infrastructure, designs must reduce overheating in line with the Cooling Hierarchy.

Actions:

- The energy report should specify the heating and ventilation strategy assumed under Baseline and Be Lean. For non-residential applications the baseline should align with the proposed heating system, i.e. if proposing an air source heat pump, this should be specified with the efficiency values set out in Part L 2021 for that system under Be Lean.

- Please identify on a plan where the MVHR units will be located within the dwellings. The units should be less than 2m away from external walls. This detail can also be conditioned.

- Demonstrate the cooling hierarchy has been followed, and specify which overheating mitigation measures are proposed to reduce the overheating risk within the proposed design:

  - Internal heat generation, i.e. heat distribution infrastructure

  - Heat entering building, i.e. shutters, trees, vegetation, blinds

  - Manage heat through thermal mass and high ceilings

  - Passive ventilation, i.e. openable windows, shallow floorplates, dual aspect, stack effect

  - Mechanical ventilation, i.e. free cooling from outside air in shade, by-pass for summer mode

Energy – Clean

The applicant is not proposing any Be Clean measures. The site is not within reasonable distance of a proposed Decentralised Energy Network (DEN). A Combined Heat and Power (CHP) plant would not be appropriate for size of development.

Energy – Green

As part of the Be Green carbon reductions, all new developments must achieve a minimum reduction of 20% from on-site renewable energy generation to comply with Policy SP4.

The application has reviewed the installation of various renewable technologies. The report concludes that air source heat pumps (ASHPs) and solar photovoltaic (PV) panels are the most viable options to deliver the Be Green requirement. A total of 0.8 tCO2 (30%) reduction of emissions are proposed under Be Green measures.

The solar array peak output would be 7.14kWp, which is estimated to produce around 5,586 kWh/year of renewable electricity per year. The array solar PV panels would be mounted on a roof area of 34 m2, at a 25° angle, oriented 131 degrees clockwise from the north.

The 85kW individual air-to-water ASHP system (min. SCOP of 3) will provide heating to the school through underfloor radiators and local extract while electric immersion heater will provide DHW.

Actions:

- Please provide some commentary on how the available roof space has been maximised to install solar PV. Has your feasibility shown that other roofs will not be viable / will they be used for other purposes?

- A living roof should be installed under the solar PV, or if this is not feasible, the roof should be light coloured to reduce solar heat gains and to improve efficiency of the solar panels.

- Please identify on the plans where the internal and external parts of the air source heat pumps will be located and how the units will be mitigated in terms of visual and noise impact.

- How much of the heating and hot water demand will be met by the proposed type of heat pump and electric storage water heater?

- Overheating

The applicant has undertaken a dynamic thermal modelling assessment in line with CIBSE BB101:2018 with London Heathrow Weather files. The report has modelled 47 rooms and spaces.

Results are listed in the table below.

|  | No of rooms/spaces passing BB101 2018 Criteria 1 | No. of rooms/spaces passing Criteria 2 (Max. Daily Deg. Hrs) | Criteria 3 (Max. DeltaT) |
| --- | --- | --- | --- |
| DSY1 2020s | 47/47 | 38/47 | 47/47 |
| DSY 2 2020s | 47/47 | 33/47 | 39/47 |
| DSY 3 2020s | 46/47 | 29/47 | 42/47 |

All room and spaces pass the overheating requirements for 2020s DSY1. To pass this, the following measures will be built:

- Natural and mechanical ventilation through openable windows and hybrid ventilation units in occupied spaces.

- External shading via horizontal and vertical brise.

- Ground floor glazing in the refurbished existing portion of the development to be side-hung openable to 90 degrees without restrictors.

- Ground floor glazing in the extension portion of the building to be side-hung and restricted to 130mm.

- All other vertical glazing to be side hung and restricted to 300mm for the whole building.

- Internal blinds included in all occupied spaces.

- Carbon Offset Contribution

A carbon shortfall of 1.7 tCO2/year remains. The remaining carbon emissions will need to be offset at £95/tCO2 over 30 years.

- Overall Sustainability

Policy DM21 of the Development Management Document requires developments to demonstrate sustainable design, layout and construction techniques. The Sustainability section in the report sets out the proposed measures to improve the sustainability of the scheme, including transport, health and wellbeing, materials and waste, water consumption, flood risk and drainage, biodiversity, climate resilience, energy and CO2 emissions and landscape design.

The development proposed to target the BREEAM LE 02, LE 03 and LE 04.

The development is not proposing any parking and is encouraging sustainable forms of transportation. A minimum of 20 cycle storage spaces are proposed which will be covered, secure and lit. Furthermore, incentives, awareness, and other measures are put in place to encourage active travel.

The development has targeted BREEAM Mat01 by undertaking a BREEAM-compliant Life Cycle Assessment (LCA) using OneClick LCA software. The RIBA Stage 2 work is complete and submitted to BRE. This includes analysis of the superstructure, substructure and hard landscaping, and building services.

A Sustainable Procurement Plan has been developed to guide the team as the project develops, including choosing products with responsible sourcing accreditation (such as ISO 14001, BES 6001, FSC, PEFC), and Environmental Product Declarations. All timber used on the site is proposed to be ‘Legal’ and ‘Sustainable’ as per the UK Government’s Timber Procurement Policy (TPP).

Sustainability - Non-Domestic BREEAM Requirement

Policy SP4 requires all new non-residential developments to achieve a BREEAM rating ‘Very Good’ (or equivalent), although developments should aim to achieve ‘Excellent’ where achievable.

The applicant has prepared a BREEAM Pre-Assessment Report for the development. Based on this report, a score of 69.25% is expected to be achieved, equivalent to ‘Very Good’ rating. All Excellent minimum standards have been targeted as part of the target score and the assessment will be reviewed as the design progresses to see if an Excellent rating is achievable.

Sustainability – Urban Greening and Biodiversity

All development sites must incorporate urban greening within their fundamental design, in line with London Plan Policy G5. London Plan Policy G6 and Local Plan Policy DM21 require proposals to manage impacts on biodiversity and aim to secure a biodiversity net gain. Additional greening should be provided through high-quality, durable measures that contribute to London’s biodiversity and mitigate the urban heat island impact. This should include tree planting, shrubs, hedges, living roofs, and urban food growing. Specifically, living roofs and walls are encouraged in the London Plan. Amongst other benefits, these will increase biodiversity and reduce surface water runoff.

All landscaping proposals and living roofs should stimulate a variety of planting species. Mat-based, sedum systems are discouraged as they retain less rainfall and deliver limited biodiversity advantages. The growing medium for extensive roofs must be 120-150mm deep, and at least 250mm deep for intensive roofs (these are often roof-level amenity spaces) to ensure most plant species can establish and thrive and can withstand periods of drought. Living walls should be rooted in the ground with sufficient substrate depth.

Living roofs are supported in principle, subject to detailed design. Details for living roofs will need to be submitted as part of a planning condition.

- Conclusion

Overall, it is considered that the application cannot currently be supported from a carbon management and sustainability point of view.

Planning Obligations Heads of Terms

- Payment of carbon offset contribution prior to the above ground construction works at £4,845, based on £2,850 per tonne of carbon emissions.

Planning Conditions

To be secured (with detailed wording TBC)

- Energy strategy

- BREEAM Certificates

- Living roof

- Sustainability

- Overheating