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	Our ref: HGY/2022/1772
Contact: Samuel Uff

Date: 02/08/2023

	Town and Country Act 1990 (As amended)

	Location:
	Hornsey Town Hall, The Broadway, London, N8 9JJ

	Proposal:
	Approval of details pursuant to condition 34 (Combined Heat and Power Details) attached to planning permission HGY/2017/2220 (revised details following approval HGY/2019/1438)

	Wording of condition:
	Prior to the commencement of the development (excepting demolition) details of the Combined Heat and Power (CHP) facility and associated infrastructure shall be submitted in writing to and for approval by the Local Planning Authority. The detail shall include:

a) location of the energy centre;
b) specification of equipment;
c) flue arrangement;
d) operation/management strategy; and
e) the method of how the facility and infrastructure shall be designed to allow for the future connection to any neighbouring heating network (including the proposed connectivity location, punch points through structure and route of the link)

The heat and hot water loads for the units on the site shall provide for no less than the total C02 reduction: Block A: 30.2%, Block B: 32.4%, and the Mews: 32.4%. The CHP system shall contribute a minimum of 75% of heat.

The details must demonstrate that the unit to be installed complies with the emissions standards as set out in the London Plan SPG Sustainable Design and Construction for Band B. The details shall also include a CHP Information Form.

The Combined Heat and Power facility and infrastructure shall be install in accordance with approved details and maintained thereafter. The system shall be operational prior to the first residential occupation of the development, unless approved in writing by the Local Planning Authority.

REASON: To ensure the facility and associated infrastructure are provided and allow for the future connection to a district system



Carbon Management Response 02/08/2023

Documents submitted:
· HGY0220256 34 (Combined Heat and Power (CHP) facility)
· 10687-M-04-BM-0007 Energy Centre Schematic C5 dated 03/02/2022
· Heating Distribution Schematic Hotel & Town Hall C1 dated 16/07/2021
· Heating Distribution Schematic Block A C3 dated 14/09/2021
· Heating Distribution Schematic Block B C1 dated 11/10/2021
· Heating Distribution Schematic Mews and Annex C1 dated 01/06/2021
· Heating Substation Schematic Mews and Annex C1 dated 15/04/2021
· Mechanical Services Layout Block A Energy Centre C2 dated 24/03/2023
· Heating Distribution Schematic Town Hall C1 dated 16/07/2021
· Hot Water Distribution Schematic Town Hall C1 dated 28/01/2022
· Hot Water Distribution Schematic Hotel C1 dated 28/01/2022
· Gas & Flue Schematic Block A C2 dated 02/06/2021
· Other supporting documents

Response:
The applicant submitted documents in the form of schematic diagrams and plans provides the location of the energy centre, specifications of the equipment, flue arrangement and future connection designs. The operation and management strategy are confirmed to be as per the Bosch premium service contract. 

The details must demonstrate that the unit to be installed complies with the emissions standards as set out in the London Plan SPG Sustainable Design and Construction for Band B. The details shall also include a CHP Information Form.

Action:
· Please provide the detailed specification of the proposed CHP equipment. 
· Please provide the complete flue arrangement plan showing the location of the flue terminations and their respective termination heights. 
· Please provide more information on operation and management strategy. On failure of CHP, what alternative strategy will be applied? Also, what is the decarbonisation strategy?
· Demonstrate how the units to be installed complies with the emission standards as set out in the London Plan SPG Sustainable Design and Construction for Band B. Also, include a CHP information form. 

Conclusion
Further information is required so we therefore do not recommend discharging Condition 34. The applicant should provide a response to all the points raised above and issue updated plans/information where required.


