|  |  | Our ref: HGY/2024/0921 Contact: Eunice Huang Date: 10/06/2024 |
| --- | --- | --- |
| Town and Country Act 1990 (As amended) |  |  |
| Location: | Harcourt House, 16-17 Haringey Park, Hornsey, London, N8 9JB |  |
| Proposal: | Erection of one additional storey at roof level to existing building to provide two self-contained apartments, plant and associated works |  |

Carbon Management Response 06/2023

In preparing this consultation response, we have reviewed:

- Energy Strategy prepared by John Francis MEP (dated 22/03/2024) including Be Clean SAP worksheet scenarios modelling different options of heating systems and a section on sustainable measures

- Relevant supporting documents.

Required missing information:

- SAP worksheet for Be Lean scenario

- The submitted Energy Statement has no information on EUI and space heating demand

- GLA’s Carbon Emission Reporting Spreadsheet

- Overheating Assessment

- Summary

Only one unit has been modelled, and it is assumed that results apply to both proposed dwellings. The Energy Statement proposes 4 carbon reduction options, and it is not clear which one will be progressed.

The development achieves a reduction of 54.75% carbon dioxide emissions on site (based on option 4 using high retention electric panel heating with heat pump hot water cylinder), which is supported in principle. Some clarifications must be provided with regard to the Energy Strategy and Sustainable measures. Missing Overheating Strategy should be provided. Appropriate planning conditions will be recommended once this information has been provided.

The applicant should note that London Plan Policies should still be taken into account, and that Haringey Policy SP4 applies to all developments, including minor applications. This means that there is a zero-carbon policy requirement (see Section 2), and a requirement to deliver a 20% saving with renewable energy generation on site (see Section 2 Energy Green). The policy analysis on p. 3 is therefore not correct or representative of the development plan.

- Energy – Overall

Policy SP4 of the Local Plan Strategic Policies, requires all new development to be zero carbon (i.e. a 100% improvement beyond Part L (2021)). The London Plan (2021) further confirms this in Policy SI2.

The overall predicted reduction in CO2 emissions for the development shows an improvement of approximately 54.75% in carbon emissions (based on option 4), from the Baseline development model (which is Part L 2021 compliant). The amount of annual saving of approximately tonnes of CO2 from a baseline in tCO2/year is to be provided for the whole development.

In addition, the applicant is referring to multiple versions of Part L. Only Part L 2021 should be used to calculate the notional and proposed development.

| Residential |  |  |  |
| --- | --- | --- | --- |
|  | Total regulated emissions (Tonnes CO2 / year) | CO2 savings (Tonnes CO2 / year) | Percentage savings (%) |
| Part L 2021 baseline | TBC |  |  |
| Be Lean |  | TBC | TBC% |
| Be Clean |  | N/A | TBC% |
| Be Green |  | TBC | 54.75% |
| Cumulative savings |  | TBC | % |
| Carbon shortfall to offset (tCO2) | TBC |  |  |
| Carbon offset contribution | £95 x 30 years x TBC tCO2/year = £ TBC |  |  |

Action:

- Please submit SAP worksheet Be Lean scenario.

- Please submit the GLA’s Carbon Emission Reporting Spreadsheet.

- Please report the baseline emissions and savings in tCO2/year.

- Please confirm the modelled notional heating system, this should be a gas boiler system.

- One of the two flats has been used as a sampled unit for energy modelling. Applicant to note the total carbon emissions in tCO2 will need to include the emission of both units.

- The carbon shortfall will be required to offset based on the calculation of £95 for 30 years per tCO2. Applicant to confirm the carbon shortfall in tCO2 and the carbon offset contribution if applicable.

- The Energy Strategy report has concluded that option 3 (Exhaust air heat pump) or option 4 (high retention electric panel heating with heat pump hot water cylinder) are both viable. The option with less percentage saving has been used for the purpose of preparing this Carbon Management Report, i.e. Option 4 is used.

- The development should propose one option only, and this should be an option that maximises the carbon savings on site. Applicant needs to confirm which option will be implemented and therefore the reduction in CO2 emissions.

Energy Use Intensity / Space Heating Demand

Applications are required to report on the total Energy Use Intensity and Space Heating Demand, in line with the GLA Energy Assessment Guidance (June 2022). The Energy Strategy should follow the reporting template set out in Table 5 of the guidance, including what methodology has been used. EUI is a measure of the total energy consumed annually, but should exclude on-site renewable energy generation and energy use from electric vehicle charging.

|  | Proposed Development | GLA Benchmark |
| --- | --- | --- |
| Building type | Residential | Residential |
| EUI | TBC | Meets/Does not meet GLA benchmark of 35kWh/m2/year |
| SHD | TBC | Meets/Does not meet GLA benchmark of 15 kWh/m2/year |
| Methodology used | SAP 10 |  |

Actions:

- What is the calculated Energy Use Intensity (excluding renewable energy)? How does this perform against GLA benchmarks, i.e. at 35kWh/m2/year? Please submit the information in line with the GLA’s reporting template.

- What is the calculated space heating demand? How does this perform against the GLA benchmark of 15 kWh/m2/year? Please submit the information in line with the GLA’s reporting template.

Energy – Lean

The applicant has not provided the information on saving of carbon emissions (in tCO2 and %) through improved energy efficient standards in key elements of the build. The application should achieve a saving beyond 10% as set in London Plan Policy SI2. There is currently insufficient information available for review to determine if the application can be supported or not.

The following u-values, g-values and air tightness are proposed:

| Floor u-value | TBC (There are existing residential units below) |
| --- | --- |
| External wall u-value | 0.15 W/m2K |
| Roof u-value | 0.10 W/m2K |
| Door u-value | 1.00 W/m2K |
| Window u-value | 1.30 W/m2K |
| G-value | 0.4-0.6 |
| Air permeability rate | TBC – 4-10 m3/hm2 @ 50Pa |
| Ventilation strategy | TBC |
| Thermal bridging | TBC |
| Low energy lighting | 100% |
| Heating system Be Lean only | Individual gas boiler (92.3% efficient), |
| Thermal mass | TBC |
| Space heating requirement | TBC kWh/m2/year |
| Fabric energy efficiency improvement | 8.72% |

London Plan Policy SI4 requires developments to minimise adverse impacts on the urban heat island, reduce the potential for overheating and reduce reliance on air conditioning systems. Through careful design, layout, orientation, materials and incorporation of green infrastructure, designs must reduce overheating in line with the Cooling Hierarchy.

Actions:

- Applicant to confirm if they have achieved a saving 10% through fabric improved energy efficient standards in key elements of the build and demonstrate by providing SAP worksheet in Be Lean scenario.

- What is the proportion of glazed area? Consider following the LETI Climate Emergency Design Guide principles in façade design.

- There are currently no South facing windows. The proposed dwellings are effectively single aspect and the applicant should consider to improve opportunities to increase daylight (sensitively in the context of Conservation area) and cross ventilation.

- There is a discrepancy of the proposed air permeability target. The Energy Strategy has indicated the target is 7-10 m3/hm2 @ 50Pa  (page 4), and 4 m3/hm2 @ 50Pa (page 5) but SAP worksheets have based on 5 m3/hm2 @ 50Pa. Please confirm if a lower air permeability rate can be achieved.

- Demonstrate the cooling hierarchy has been followed, and specify which overheating mitigation measures are proposed to reduce the overheating risk within the proposed design:

  - Internal heat generation, i.e. heat distribution infrastructure

  - Heat entering building, i.e. shutters, trees, vegetation, blinds

  - Manage heat through thermal mass and high ceilings

  - Passive ventilation, i.e. openable windows, shallow floorplates, dual aspect, stack effect

  - Mechanical ventilation, i.e. free cooling from outside air in shade, by-pass for summer mode

- The external wall U-value can be lowered, this will help to exceed the 10% reduction through fabric improved energy efficiency and reduce the risk of overheating.

- Applicant to confirm if the proposed floor will have insulation. Even though the proposed floor is on top of existing dwellings which are supposedly heated, the integration of floor insulation will help to mitigate heat loss from the development in the event that the dwellings below are unoccupied.

Energy – Clean

The applicant is not proposing any Be Clean measures. The site is not within reasonable distance of a proposed Decentralised Energy Network (DEN). A Combined Heat and Power (CHP) plant would not be appropriate for size of development.

Energy – Green

As part of the Be Green carbon reductions, all new developments must achieve a minimum reduction of 20% from on-site renewable energy generation to comply with Policy SP4.

The application has reviewed the installation of various renewable technologies. Various options are proposed for this development:

- Mains gas boiler (heating and hot water), assuming a 89.9% efficient boiler and would need to use a 2.5 kWp PV system to offset the primary energy amount

- Air source heat pump (250% efficiency) with an integrated 120L cylinder, assuming a Daikin Altherma internal and external unit

- Exhaust air heat pump, assuming a NIBE fighter F470 unit with integrated water heating (and immersion) and whole-house ventilation

- High retention electric panel heating with heat pump hot water cylinder, assuming a Dimplex Edel cylinder with external air supplied via ductwork to a hot water heat pump internally.

The report concludes that either option 3 or option 4 are the most viable options to deliver the Be Green requirement. It is expected that Option 3 could deliver the highest savings (63%, compared to 58% for Option 2 and 55% for Option 4).

No solar photovoltaic (PV) panels are proposed currently, this does not meet the 20% minimum reduction from on-site renewable energy generation requirements.

Actions:

- The development should propose one option only, and this should be an option that maximises the carbon savings on site.

- Direct electric panels are not acceptable unless it can be demonstrated that the homes will meet Passivhaus-standard levels of fabric efficiency.

- Please provide solar photovoltaic panels to meet and aim to exceed the 20% minimum reduction from on-site renewable energy generation requirements. The development should maximize its renewable energy opportunities on site before resorting to offsetting. This may be found acceptable from a heritage perspective, but plans, sections and elevations must first demonstrate the visual appearance. The strategy should set out the proposed carbon reduction from solar PV, by providing the total output (kWp) and expected annual generation (kWh/year) and inverter capacity.

- If PV panels are provided, applications should demonstrate how they might take a demand-side response to reducing energy use. Has battery storage for the solar PV system been considered, or justify why this is not proposed.

- Please set out how much of the heating/hot water demand will be met by the proposed type of heat pump?

- Carbon Offset Contribution

The amount of carbon shortfall in tCO2/year is to be established subject to the confirmation of the heating system for the development by the applicant. The remaining carbon emissions will need to be offset at £95/tCO2 over 30 years.

- Overall Sustainability

Policy DM21 of the Development Management Document requires developments to demonstrate sustainable design, layout and construction techniques. The Sustainability section in the report sets out the proposed measures to improve the sustainability of the scheme, including transport, health and wellbeing, materials and waste, water consumption, flood risk and drainage, biodiversity, climate resilience, energy and CO2 emissions and landscape design.

Action:

- The information provided in the Sustainable Measures in the Energy Strategy is insufficient, please provide project specific information.

- The development is proposed on existing roof level, external balconies are provided as external amenity spaces to the dwelling units and there are no garden spaces. Applicant is still encouraged to provide urban greening and biodiversity enhancement measures (e.g. planters, bird boxes, bat boxes etc) on the wider site within the red line boundary.

- Specify the location and number of safe, covered, and accessible cycle parking spaces for the new residents.

- A target (%) for responsible sourced, low-impact materials used during construction.

Sustainability – Urban Greening and Biodiversity

All development sites must incorporate urban greening within their fundamental design, in line with London Plan Policy G5. London Plan Policy G6 and Local Plan Policy DM21 require proposals to manage impacts on biodiversity and aim to secure a biodiversity net gain. Additional greening should be provided through high-quality, durable measures that contribute to London’s biodiversity and mitigate the urban heat island impact. This should include tree planting, shrubs, hedges, living roofs, and urban food growing. Specifically, living roofs and walls are encouraged in the London Plan. Amongst other benefits, these will increase biodiversity and reduce surface water runoff.

- Conclusion

Overall, it is considered that the application can be supported from a carbon management and sustainability point of view. Applicant is required to confirm which heating system will be implemented in order to formulate the carbon offset contribution.

Planning Obligations Heads of Terms

- Payment of carbon offset contribution prior to the above ground construction, which will be confirmed prior to the determination of the application once the applicant has responded to the points above, and will be based on £2,850 per tonne of carbon emissions.

Planning Conditions

To be secured (with detailed wording TBC):

- Energy Strategy

- Overheating