|  |  | Our ref: HGY/2024/0361 Contact: Sarah Madondo Date: 18/03/2024 |
| --- | --- | --- |
| Town and Country Act 1990 (As amended) |  |  |
| Location: | Flat B, 2 Vartry Road, Tottenham, London, N15 6PT |  |
| Proposal: | Demolition or existing self-contained studio and erection of self-contained studio |  |

Carbon Management Response 18/03/2024

In preparing this consultation response, we have reviewed:

- Energy Statement prepared by Achieve Green (dated 12 March 2023)

- Relevant supporting documents.

- Summary

The development achieves a reduction of 101% carbon dioxide emissions on site, which is supported in principle. Planning conditions have been recommended to secure the benefits of the scheme.

- Energy – Overall

Policy SP4 of the Local Plan Strategic Policies, requires all new development to be zero carbon (i.e. a 100% improvement beyond Part L (2021)). The London Plan (2021) further confirms this in Policy SI2.

The overall predicted reduction in CO2 emissions for the development shows an improvement of approximately 101% in carbon emissions, from the Baseline development model (which is Part L 2021 compliant). This represents an annual saving of approximately 1 tonnes of CO2 from a baseline of 0.9 tCO2/year.

| Residential |  |  |  |
| --- | --- | --- | --- |
|  | Total regulated emissions (Tonnes CO2 / year) | CO2 savings (Tonnes CO2 / year) | Percentage savings (%) |
| Part L 2021 baseline | 0.9 |  |  |
| Be Lean | 0.8 | 0.1 | 14% |
| Be Clean | 0.8 | 0 | 0% |
| Be Green | 0.0 | 0.8 | 87% |
| Cumulative savings |  | 1.0 | 101% |
| Carbon shortfall to offset (tCO2) | 0 |  |  |

Action:

- Please submit the SAP sheets for the Baseline and Be Green scenarios.

Energy – Lean

The applicant has proposed a saving of 0.1 tCO2 in carbon emissions (14%) through improved energy efficiency standards in key elements of the build. This goes beyond the minimum 10% reduction respectively set in London Plan Policy SI2 for major applications, so this is supported.

The following u-values, g-values and air tightness are proposed:

| Floor u-value | 0.10 W/m2K |
| --- | --- |
| External wall u-value | 0.18 W/m2K |
| Roof u-value | 0.13 W/m2K |
| Window u-value | 1.20 W/m2K |
| Air permeability rate | 3.5 m3/hm2 @ 50Pa |
| Ventilation strategy | Natural ventilation Mechanical ventilation with heat recovery (90% efficiency; SPF of 0.5 W/l/s) |
| Thermal bridging | Accredited Construction Details; y = 0.07 |
| Low energy lighting | 80 lm/W |

London Plan Policy SI4 requires developments to minimise adverse impacts on the urban heat island, reduce the potential for overheating and reduce reliance on air conditioning systems. Through careful design, layout, orientation, materials and incorporation of green infrastructure, designs must reduce overheating in line with the Cooling Hierarchy.

Action:

- Please comment on how the application reduces overheating risk.

- Please confirm the improvement on the Target Fabric Energy Efficiency?

Energy – Clean

The applicant is not proposing any Be Clean measures. The site is not within reasonable distance of a proposed Decentralised Energy Network (DEN). A Combined Heat and Power (CHP) plant would not be appropriate for size of development.

Energy – Green

As part of the Be Green carbon reductions, all new developments must achieve a minimum reduction of 20% from on-site renewable energy generation to comply with Policy SP4.

The application has reviewed the installation of various renewable technologies. The report concludes that an air source heat pump (ASHPs) and solar photovoltaic (PV) panels are the most viable options to deliver the Be Green requirement. A total of 0.8 tCO2 (87%) reduction of emissions are proposed under Be Green measures.

The solar array peak output would be 3.8 kWp. The individual air-to-water ASHP systems will provide hot water and heating to the dwelling.

Actions:

- Please submit a roof plan showing the indicative PV layout. What is the expected annual energy generation?

- A living roof should be installed under the solar PV, or if this is not feasible, the roof should be light coloured to reduce solar heat gains and to improve efficiency of the solar panels.

- Please identify on the plans where the internal and external parts of the air source heat pumps will be located and how the units will be mitigated in terms of visual and noise impact. What is the modelled efficiency for the ASHP?

- Overall Sustainability

Policy DM21 of the Development Management Document requires developments to demonstrate sustainable design, layout and construction techniques. No Sustainability Report has been provided.

Action:

- It is recommended that a living roof is installed on the flat roof areas.

- The site should also provide space for safe cycle parking.

- Conclusion

Overall, it is considered that the application can be supported in principle from a carbon management and sustainability point of view.

Planning Conditions

To be secured, and further conditions may be recommended.

Carbon Management Response 14/08/2024

In preparing this consultation response, we have reviewed:

- Energy Statement prepared by Achieve Green (dated 12 March 2023)

- Part L 2021 GLA Carbon Emission Spreadsheet screenshots

- Building Regulations England Part L (BREL) Compliance Report

Summary

The fabric energy efficiency improvement is 0.7%. The additional information confirms the proposal as above, which is supported. The planning condition below is recommended to secure the benefits of this scheme.

No carbon offset contribution is required as the development is zero carbon in policy terms.

Energy Strategy

The development hereby approved shall be constructed in accordance with the Energy Strategy by Achieve Green (dated March 2024) delivering a minimum 100% improvement on carbon emissions over 2021 Building Regulations Part L, with high fabric efficiencies, an air source heat pump (ASHP) and a minimum 3.8 kWp solar photovoltaic (PV) array. 

(a) Prior to above ground construction, details of the Energy Strategy shall be submitted to and approved by the Local Planning Authority. This must include:

- Confirmation of how this development will meet the zero-carbon policy requirement in line with the Energy Hierarchy, confirming the As Designed SAP calculations;

- Confirmation of the necessary fabric efficiencies to achieve a minimum 14% reduction;

- Location, specification and efficiency of the proposed ASHP (Coefficient of Performance, Seasonal Coefficient of Performance, and the Seasonal Performance Factor), with plans showing the ASHP pipework and noise and visual mitigation measures;

- Specification and efficiency of the proposed Mechanical Ventilation and Heat Recovery (MVHR), with plans showing the rigid MVHR ducting and location of the unit;

- Details of the PV, demonstrating the roof area has been maximised, with the following details: a roof plan; the number, angle, orientation, type, and efficiency level of the PVs; how overheating of the panels will be minimised; their peak output (kWp)

- Specification of any additional equipment installed to reduce carbon emissions.

The development shall be carried out strictly in accordance with the details so approved prior to first operation and shall be maintained and retained for the lifetime of the development. The solar PV array shall be installed with monitoring equipment prior to completion and shall be maintained at least annually thereafter.

Reason: To ensure the development reduces its impact on climate change by reducing carbon emissions on site in compliance with the Energy Hierarchy, and in line with London Plan (2021) Policy SI2, and Local Plan (2017) Policies SP4 and DM22.

Overheating

Prior to above ground construction, a statement shall be submitted to and approved by the Local Planning Authority to demonstrate how the overheating risk has been minimised and mitigated on site in line with the London Plan Cooling Hierarchy. Details and specification of the mitigation measures shall be provided in support of this statement.

Reason: In the interest of reducing the impacts of climate change and mitigation of overheating risk, in accordance with London Plan (2021) Policy SI4, and Local Plan (2017) Policies SP4 and DM21.