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	Our ref: HGY/2024/0921
Contact: Eunice Huang

Date: 08/08/2025

	Town and Country Act 1990 (As amended)

	Location:
	Harcourt House, 16-17 Haringey Park, Hornsey, London, N8 9JB

	Proposal:
	Erection of one additional storey at roof level to existing building to provide two self-contained apartments, plant and associated works




Carbon Management Response 06/2024

In preparing this consultation response, we have reviewed:
· Energy Strategy prepared by John Francis MEP (dated 22/03/2024) including Be Clean SAP worksheet scenarios modelling different options of heating systems and a section on sustainable measures 
· Relevant supporting documents.

Required missing information: 
· SAP worksheet for Be Lean scenario 
· The submitted Energy Statement has no information on EUI and space heating demand
· GLA’s Carbon Emission Reporting Spreadsheet
· Overheating Assessment 

1. Summary
[bookmark: _Hlk122107763]Only one unit has been modelled, and it is assumed that results apply to both proposed dwellings. The Energy Statement proposes 4 carbon reduction options, and it is not clear which one will be progressed.

The development achieves a reduction of 54.75% carbon dioxide emissions on site (based on option 4 using high retention electric panel heating with heat pump hot water cylinder), which is supported in principle. Some clarifications must be provided with regard to the Energy Strategy and Sustainable measures. Missing Overheating Strategy should be provided. Appropriate planning conditions will be recommended once this information has been provided. 

The applicant should note that London Plan Policies should still be taken into account, and that Haringey Policy SP4 applies to all developments, including minor applications. This means that there is a zero-carbon policy requirement (see Section 2), and a requirement to deliver a 20% saving with renewable energy generation on site (see Section 2 Energy Green). The policy analysis on p. 3 is therefore not correct or representative of the development plan.

2. Energy – Overall 
Policy SP4 of the Local Plan Strategic Policies, requires all new development to be zero carbon (i.e. a 100% improvement beyond Part L (2021)). The London Plan (2021) further confirms this in Policy SI2. 

The overall predicted reduction in CO2 emissions for the development shows an improvement of approximately 54.75% in carbon emissions (based on option 4), from the Baseline development model (which is Part L 2021 compliant). The amount of annual saving of approximately tonnes of CO2 from a baseline in tCO2/year is to be provided for the whole development. 

In addition, the applicant is referring to multiple versions of Part L. Only Part L 2021 should be used to calculate the notional and proposed development.


	Residential 

	[bookmark: _Hlk100683248]
	Total regulated emissions 
(Tonnes CO2 / year) 
	CO2 savings
(Tonnes CO2 / year) 
	Percentage savings
(%)

	Part L 2021 baseline 
	TBC
	
	

	Be Lean 
	
	TBC
	TBC%

	Be Clean 
	
	N/A
	TBC%

	Be Green 
	
	TBC
	54.75%

	Cumulative savings
	
	TBC
	%

	Carbon shortfall to offset (tCO2)
	TBC
	
	

	Carbon offset contribution
	£95 x 30 years x TBC tCO2/year = £ TBC



Action:
· Please submit SAP worksheet Be Lean scenario. 
· Please submit the GLA’s Carbon Emission Reporting Spreadsheet.
· Please report the baseline emissions and savings in tCO2/year.
· Please confirm the modelled notional heating system, this should be a gas boiler system.
· One of the two flats has been used as a sampled unit for energy modelling. Applicant to note the total carbon emissions in tCO2 will need to include the emission of both units. 
· The carbon shortfall will be required to offset based on the calculation of £95 for 30 years per tCO2. Applicant to confirm the carbon shortfall in tCO2 and the carbon offset contribution if applicable. 
· The Energy Strategy report has concluded that option 3 (Exhaust air heat pump) or option 4 (high retention electric panel heating with heat pump hot water cylinder) are both viable. The option with less percentage saving has been used for the purpose of preparing this Carbon Management Report, i.e. Option 4 is used.
· The development should propose one option only, and this should be an option that maximises the carbon savings on site. Applicant needs to confirm which option will be implemented and therefore the reduction in CO2 emissions. 


[bookmark: _Hlk130228602]Energy Use Intensity / Space Heating Demand
Applications are required to report on the total Energy Use Intensity and Space Heating Demand, in line with the GLA Energy Assessment Guidance (June 2022). The Energy Strategy should follow the reporting template set out in Table 5 of the guidance, including what methodology has been used. EUI is a measure of the total energy consumed annually, but should exclude on-site renewable energy generation and energy use from electric vehicle charging. 

	
	Proposed Development
	GLA Benchmark

	Building type
	Residential
	Residential

	EUI 
	TBC
	Meets/Does not meet GLA benchmark of 35kWh/m2/year

	SHD 
	TBC
	Meets/Does not meet GLA benchmark of 15 kWh/m2/year

	Methodology used
	SAP 10
	




Actions:
· What is the calculated Energy Use Intensity (excluding renewable energy)? How does this perform against GLA benchmarks, i.e. at 35kWh/m2/year? Please submit the information in line with the GLA’s reporting template.
· What is the calculated space heating demand? How does this perform against the GLA benchmark of 15 kWh/m2/year? Please submit the information in line with the GLA’s reporting template.

Energy – Lean
The applicant has not provided the information on saving of carbon emissions (in tCO2 and %) through improved energy efficient standards in key elements of the build. The application should achieve a saving beyond 10% as set in London Plan Policy SI2. There is currently insufficient information available for review to determine if the application can be supported or not. 

The following u-values, g-values and air tightness are proposed:

	Floor u-value
	TBC (There are existing residential units below)  

	External wall u-value
	0.15 W/m2K

	Roof u-value
	0.10 W/m2K

	Door u-value
	1.00 W/m2K

	Window u-value
	1.30 W/m2K

	G-value
	0.4-0.6

	Air permeability rate
	TBC – 4-10 m3/hm2 @ 50Pa

	Ventilation strategy
	TBC

	Thermal bridging
	TBC

	Low energy lighting
	100%

	Heating system Be Lean only
	Individual gas boiler (92.3% efficient), 

	Thermal mass
	TBC

	Space heating requirement
	TBC kWh/m2/year

	Fabric energy efficiency improvement
	8.72%



London Plan Policy SI4 requires developments to minimise adverse impacts on the urban heat island, reduce the potential for overheating and reduce reliance on air conditioning systems. Through careful design, layout, orientation, materials and incorporation of green infrastructure, designs must reduce overheating in line with the Cooling Hierarchy. 

Actions:
· Applicant to confirm if they have achieved a saving 10% through fabric improved energy efficient standards in key elements of the build and demonstrate by providing SAP worksheet in Be Lean scenario. 
· [bookmark: _Hlk122108176]What is the proportion of glazed area? Consider following the LETI Climate Emergency Design Guide principles in façade design. 
· There are currently no South facing windows. The proposed dwellings are effectively single aspect and the applicant should consider to improve opportunities to increase daylight (sensitively in the context of Conservation area) and cross ventilation. 
· There is a discrepancy of the proposed air permeability target. The Energy Strategy has indicated the target is 7-10 m3/hm2 @ 50Pa  (page 4), and 4 m3/hm2 @ 50Pa (page 5) but SAP worksheets have based on 5 m3/hm2 @ 50Pa. Please confirm if a lower air permeability rate can be achieved.
· [bookmark: _Hlk122108227]Demonstrate the cooling hierarchy has been followed, and specify which overheating mitigation measures are proposed to reduce the overheating risk within the proposed design:
· Internal heat generation, i.e. heat distribution infrastructure
· Heat entering building, i.e. shutters, trees, vegetation, blinds
· Manage heat through thermal mass and high ceilings
· Passive ventilation, i.e. openable windows, shallow floorplates, dual aspect, stack effect
· Mechanical ventilation, i.e. free cooling from outside air in shade, by-pass for summer mode 
· The external wall U-value can be lowered, this will help to exceed the 10% reduction through fabric improved energy efficiency and reduce the risk of overheating. 
· Applicant to confirm if the proposed floor will have insulation. Even though the proposed floor is on top of existing dwellings which are supposedly heated, the integration of floor insulation will help to mitigate heat loss from the development in the event that the dwellings below are unoccupied. 


Energy – Clean
[bookmark: _Hlk122109947][bookmark: _Hlk122109967]The applicant is not proposing any Be Clean measures. The site is not within reasonable distance of a proposed Decentralised Energy Network (DEN). A Combined Heat and Power (CHP) plant would not be appropriate for size of development. 

Energy – Green
As part of the Be Green carbon reductions, all new developments must achieve a minimum reduction of 20% from on-site renewable energy generation to comply with Policy SP4. 

The application has reviewed the installation of various renewable technologies. Various options are proposed for this development:
1. Mains gas boiler (heating and hot water), assuming a 89.9% efficient boiler and would need to use a 2.5 kWp PV system to offset the primary energy amount
2. Air source heat pump (250% efficiency) with an integrated 120L cylinder, assuming a Daikin Altherma internal and external unit
3. Exhaust air heat pump, assuming a NIBE fighter F470 unit with integrated water heating (and immersion) and whole-house ventilation
4. High retention electric panel heating with heat pump hot water cylinder, assuming a Dimplex Edel cylinder with external air supplied via ductwork to a hot water heat pump internally.

The report concludes that either option 3 or option 4 are the most viable options to deliver the Be Green requirement. It is expected that Option 3 could deliver the highest savings (63%, compared to 58% for Option 2 and 55% for Option 4).
No solar photovoltaic (PV) panels are proposed currently, this does not meet the 20% minimum reduction from on-site renewable energy generation requirements. 

Actions:
· The development should propose one option only, and this should be an option that maximises the carbon savings on site. 
· Direct electric panels are not acceptable unless it can be demonstrated that the homes will meet Passivhaus-standard levels of fabric efficiency.
· Please provide solar photovoltaic panels to meet and aim to exceed the 20% minimum reduction from on-site renewable energy generation requirements. The development should maximize its renewable energy opportunities on site before resorting to offsetting. This may be found acceptable from a heritage perspective, but plans, sections and elevations must first demonstrate the visual appearance. The strategy should set out the proposed carbon reduction from solar PV, by providing the total output (kWp) and expected annual generation (kWh/year) and inverter capacity.
· [bookmark: _Hlk130229277]If PV panels are provided, applications should demonstrate how they might take a demand-side response to reducing energy use. Has battery storage for the solar PV system been considered, or justify why this is not proposed. 
· [bookmark: _Hlk74057450]Please set out how much of the heating/hot water demand will be met by the proposed type of heat pump? 

3. Carbon Offset Contribution
The amount of carbon shortfall in tCO2/year is to be established subject to the confirmation of the heating system for the development by the applicant. The remaining carbon emissions will need to be offset at £95/tCO2 over 30 years. 

4. Overall Sustainability
Policy DM21 of the Development Management Document requires developments to demonstrate sustainable design, layout and construction techniques. The Sustainability section in the report sets out the proposed measures to improve the sustainability of the scheme, including transport, health and wellbeing, materials and waste, water consumption, flood risk and drainage, biodiversity, climate resilience, energy and CO2 emissions and landscape design. 

Action:
· [bookmark: _Hlk122108525]The information provided in the Sustainable Measures in the Energy Strategy is insufficient, please provide project specific information. 
· The development is proposed on existing roof level, external balconies are provided as external amenity spaces to the dwelling units and there are no garden spaces. Applicant is still encouraged to provide urban greening and biodiversity enhancement measures (e.g. planters, bird boxes, bat boxes etc) on the wider site within the red line boundary.
· Specify the location and number of safe, covered, and accessible cycle parking spaces for the new residents.
· A target (%) for responsible sourced, low-impact materials used during construction. 


Sustainability – Urban Greening and Biodiversity
[bookmark: _Hlk108865970]All development sites must incorporate urban greening within their fundamental design, in line with London Plan Policy G5. London Plan Policy G6 and Local Plan Policy DM21 require proposals to manage impacts on biodiversity and aim to secure a biodiversity net gain. Additional greening should be provided through high-quality, durable measures that contribute to London’s biodiversity and mitigate the urban heat island impact. This should include tree planting, shrubs, hedges, living roofs, and urban food growing. Specifically, living roofs and walls are encouraged in the London Plan. Amongst other benefits, these will increase biodiversity and reduce surface water runoff. 


5. Conclusion
Overall, it is considered that the application can be supported from a carbon management and sustainability point of view. Applicant is required to confirm which heating system will be implemented in order to formulate the carbon offset contribution. 


Planning Obligations Heads of Terms
· Payment of carbon offset contribution prior to the above ground construction, which will be confirmed prior to the determination of the application once the applicant has responded to the points above, and will be based on £2,850 per tonne of carbon emissions.

Planning Conditions 
[bookmark: _Hlk122108708]To be secured (with detailed wording TBC):
· Energy Strategy
· Overheating 


Carbon Management Response 18/03/2025

In preparing this consultation response, we have reviewed:
· Energy Strategy prepared by John Francis MEP revision PR1v (dated 06/08/2024) including Part L worksheets and GLA worksheets in the appendices

1. Summary
The development achieves a reduction of 63.38 % carbon dioxide emissions on site (0.95 tCO2) from a Building Regulations Part L 2021 compliant building. This is supported in principle. Planning conditions have been recommended to secure the benefits of the scheme. 

2. Energy – Overall 
The revised ES has confirmed that exhaust air heat pump (EAHP) has been proposed, the carbon reductions across all stages and the overall reduction have been updated accordingly. 

	Residential 

	
	Total regulated emissions 
(Tonnes CO2 / year) 
	CO2 savings
(Tonnes CO2 / year) 
	Percentage savings
(%)

	Part L 2021 baseline 
	1.49
	
	

	Be Lean 
	1.11
	0.39
	25.84%

	Be Clean 
	0.57
	0.53
	35.69%

	Be Green 
	0.55
	0.03
	1.86%

	Cumulative savings
	
	0.95
	63.38%

	Carbon shortfall to offset (tCO2)
	0.55
	
	

	Carbon offset contribution
	£95 x 30 years x 0.55 tCO2/year = £ 1,568



Energy Use Intensity / Space Heating Demand
	
	Proposed Development
	GLA Benchmark

	Building type
	Residential
	Residential

	EUI 
	34.08 kWh/m2/year
	Meets GLA benchmark of 35kWh/m2/year

	SHD 
	25.89 kWh/m2/year

	Does not meet GLA benchmark of 15 kWh/m2/year

	Methodology used
	SAP 10
	



Energy – Lean
The ES has provided the following revised fabric efficiencies: 
	G-value
	0.45

	Air permeability rate
	4m3/hm2 @ 50Pa

	Thermal bridging
	Accredited details 



Applicant has not provided the missing Overheating Strategy. This will be conditioned. 

Actions:
· Applicant to confirm the ventilation strategy. EAHP has designed to work in conjunction with MVHR, please confirm if MVHRs have been proposed. This will be conditioned. 
· Applicant to clarify if the provided Part L worksheets of the two units are only for the Be Green scenario. SAP worksheets for Be Lean scenario should be provided as well. 
· Applicant to provide the Overheating Strategy to demonstrate the cooling hierarchy has been followed, and specify which overheating mitigation measures are proposed to reduce the overheating risk within the proposed design:
· Internal heat generation, i.e. heat distribution infrastructure
· Heat entering building, i.e. shutters, trees, vegetation, blinds
· Manage heat through thermal mass and high ceilings
· Passive ventilation, i.e. openable windows, shallow floorplates, dual aspect, stack effect
· Mechanical ventilation, i.e. free cooling from outside air in shade, by-pass for summer mode 

Energy – Clean
The applicant has incorrectly included the benefits of EAHP under Be Clean, it should be modelled under the Be Green scenario.

Energy – Green
	Proposed Renewable technologies
	Type
	Specification

	Main space heating system and DHW system
	Air source heat pump
	Individual / Communal
Exhaust heat pump
SCOP TBC

	Solar PV residential
	Peak output
	3.8 kWp covering 16.4 m2

	
	Renewable electricity produced per year
	3279.40 kWh/year (equivalent to a reduction of 0.761 tCO2/year), output to be split between the two units.  

	
	Number of panels
	10 

	
	Battery storage capacity
	N/A



Actions:
· Applicant to confirm if EAHP will provide 100% of the space heating and DHW demands. 
· Applicant if the proposed EAHPs are individual or communal.  
· In the Be Green section of the ES, it has stated the PV output is equivalent to 0.761 tCO2/year, this is supported. However this does not tally with the Be Green reduction in the summary table which currently reports only a saving of 0.03 tCO2/year. Applicant to clarify. 
· Applicant to confirm if there is battery storage capacity for the PV system. 

3. Carbon Offset Contribution
[bookmark: _Hlk188607429][bookmark: _Hlk188607453]A carbon offset contribution of £1,568 is requested to offset the shortfall in emissions that could not be delivered on site. This is calculated at £95 per tCO2 over 30 years.

4. Conclusion
Overall, it is considered that the application can be supported from a carbon management and sustainability point of view. 

5. Securing Benefits

Planning Obligations Heads of Terms
Payment of carbon offset contribution prior to the above ground construction works at £1,568, based on £2,850 per tonne of carbon emissions. 

Planning Conditions 
Energy Strategy
The development hereby approved shall be constructed in accordance with the Energy Strategy by John Francis MEP revision PR1v (dated 06/08/2024) delivering a minimum 63.38% improvement on carbon emissions over 2021 Building Regulations Part L, with high fabric efficiencies, exhaust air heat pumps (EAHPs) and a minimum 3.8 kWp solar photovoltaic (PV) array. 

(a) Prior to above ground construction, details of the Energy Strategy shall be submitted to and approved by the Local Planning Authority. This must include:
· [bookmark: _Hlk71823736]Confirmation of how this development will meet the zero-carbon policy requirement in line with the Energy Hierarchy;
· Confirmation of the necessary fabric efficiencies to achieve a minimum 25.84% reduction, including details to reduce thermal bridging;
· Location, specification and efficiency of the proposed EAHPs (Coefficient of Performance, Seasonal Coefficient of Performance, and the Seasonal Performance Factor), with plans showing the EAHPs pipework and noise and visual mitigation measures;
· Specification and efficiency of the proposed Mechanical Ventilation and Heat Recovery (MVHR), with plans showing the rigid MVHR ducting and location of the unit;
· Details of the PV, demonstrating the roof area has been maximised, with the following details: a roof plan; the number, angle, orientation, type, and efficiency level of the PVs; how overheating of the panels will be minimised; their peak output (kWp)
· [bookmark: _Hlk122110588]Specification of any additional equipment installed to reduce carbon emissions.
The development shall be carried out strictly in accordance with the details so approved prior to first operation and shall be maintained and retained for the lifetime of the development. The solar PV array shall be installed with monitoring equipment prior to completion and shall be maintained at least annually thereafter.

[bookmark: _Hlk122110615](b) The solar PV arrays and EAHPs must be installed and brought into use prior to first occupation of the development. Six months following the first occupation of the development, evidence that the solar PV arrays have been installed correctly and are operational shall be submitted to and approved by the Local Planning Authority, including photographs of the solar array, installer confirmation, an energy generation statement for the period that the solar PV array has been installed, and a Microgeneration Certification Scheme certificate.

Reason: To ensure the development reduces its impact on climate change by reducing carbon emissions on site in compliance with the Energy Hierarchy, and in line with London Plan (2021) Policy SI2, and Local Plan (2017) Policies SP4 and DM22.

[bookmark: _Hlk122110647]Overheating 
Prior to above ground construction, a statement shall be submitted to and approved by the Local Planning Authority to demonstrate how the overheating risk has been minimised and mitigated on site in line with the London Plan Cooling Hierarchy. Details and specification of the mitigation measures shall be provided in support of this statement.

Reason: In the interest of reducing the impacts of climate change and mitigation of overheating risk, in accordance with London Plan (2021) Policy SI4, and Local Plan (2017) Policies SP4 and DM21.


Carbon Management Response 08/08/2024

In preparing this consultation response, we have reviewed:
· Energy Strategy prepared by John Francis MEP revision PR4v (dated 27/06/2025) including high level TM59 overheating assessment. 

1.	Summary
The development achieves a reduction of 61.53% carbon dioxide emissions on site (1.09 tCO2) from a Building Regulations Part L 2021 compliant building. This is supported in principle. Some clarifications must be provided with regard to Energy Statement and Overheating Assessment. This can be addressed prior to determination or through planning conditions. 

	Residential 

	
	Total regulated emissions 
(Tonnes CO2 / year) 
	CO2 savings
(Tonnes CO2 / year) 
	Percentage savings
(%)

	Part L 2021 baseline 
	1.77
	
	

	Be Lean 
	1.31
	0.46
	25.84%

	Be Clean 
	0.68
	0.63
	35.69%

	Be Green 
	0.68
	0.00
	0%

	Cumulative savings
	
	1.09
	61.53%

	Carbon shortfall to offset (tCO2)
	0.68
	
	

	Carbon offset contribution
	£95 x 30 years x 0.68 tCO2/year = £ 1,938



Energy – Lean
Applicant has confirmed a centralised system (MVHR or MEV) will be provided.

Energy – Green
The applicant has provided further clarification on the proposed PV system: 
[image: A table with numbers and text

AI-generated content may be incorrect.]

Overheating
The submitted OH assessment has concluded that the initial model has shown a minor overheating risks and that only section 1a of the Part O criterion was failing using a simplified Part O method.
Based a high level TM59 modelling, the applicant has suggested the following options to mitigation OH risks including: 
· Providing additional fresh air
· Adding fixed shading to external facades
· Adding blinds natural shading
· Adding a cooling coil to the MVHR system

Energy Strategy Actions:
Energy modelling:
· Please submit the GLA’s Carbon Emission Reporting Spreadsheet in excel format. 
· Please submit SAP worksheet for Be Lean scenario. 
· Applicant should ensure the energy modelling of the proposed floor area and the windows in alignment with the latest proposed drawings. 
Be Lean:
· Applicant should confirm if they are proposing MVHR or MEV. 
Be Clean:
· The applicant has not proposed any Be Clean measures, there should be no carbon saving under Be Clean scenario. The relevant carbon benefits of using EAHP and PV system should be modelled under Be Green. 
Be Green: 
· The provision of PV system is supported in principle. However applicant has not addressed the previous comments re inconsistency of the proposed PV system and the carbon saving as modelled under Be Green stage. Applicant should provide a clarification. 
Overheating: 
· Applicant has provided a summary of preliminary Part O and high-level TM59 modelling, and it has identified a minor overheating risk with a suggestion of few options to mitigate OH risk.
· While a minor application is not required to submit TM59 OH analysis, applicant is required to demonstrate the development has been designed according to the Cooling Hierarchy by providing an Overheating Strategy.  
· Applicant should demonstrate the passive measures have been prioritised, active cooling is strongly discouraged and should be the last resort. 
· Applicant should confirm their strategy to mitigate OH risk. This will be conditioned. 

2.	Conclusion
Overall, it is considered that the principle of the application can be supported from a carbon management and sustainability point of view. Further clarifications and details should be provided prior to determination or addressed through planning conditions. 

3.	Securing Benefits

Planning Obligations Heads of Terms
Payment of carbon offset contribution prior to the above ground construction works at 1,938, based on £2,850 per tonne of carbon emissions. 

Planning Conditions 
Energy Strategy
The development hereby approved shall be constructed in accordance with the Energy Strategy by John Francis MEP revision PR4v (dated 27/06/2025) delivering a minimum 61.53% improvement on carbon emissions over 2021 Building Regulations Part L, with high fabric efficiencies, exhaust air heat pumps (EAHPs) and a minimum 4.05 kWp solar photovoltaic (PV) array. 

Should the zero-carbon target not be achieved on site through energy efficiency measures (following the Energy Hierarchy of lean, clean and green measures), then any shortfall should be offset at the cost of £2,850 per tonne of carbon.  

(a) Prior to above ground construction, details of the Energy Strategy shall be submitted to and approved by the Local Planning Authority. This must include:
· Confirmation of how this development will meet the zero-carbon policy requirement in line with the Energy Hierarchy;
· Confirmation of the necessary fabric efficiencies to achieve a minimum 25.84% reduction, including details to reduce thermal bridging;
· Location, specification and efficiency of the proposed EAHPs (Coefficient of Performance, Seasonal Coefficient of Performance, and the Seasonal Performance Factor), with plans showing the EAHPs pipework and noise and visual mitigation measures;
· Specification and efficiency of the proposed Mechanical Ventilation and Heat Recovery (MVHR), with plans showing the rigid MVHR ducting and location of the unit;
· Details of the PV, demonstrating the roof area has been maximised, with the following details: a roof plan; the number, angle, orientation, type, and efficiency level of the PVs; how overheating of the panels will be minimised; their peak output (kWp);
· Specification of any additional equipment installed to reduce carbon emissions.
The development shall be carried out strictly in accordance with the details so approved prior to first operation and shall be maintained and retained for the lifetime of the development. The solar PV array shall be installed with monitoring equipment prior to completion and shall be maintained at least annually thereafter.

(b) The solar PV arrays and EAHPs must be installed and brought into use prior to first occupation of the development. Six months following the first occupation of the development, evidence that the solar PV arrays have been installed correctly and are operational shall be submitted to and approved by the Local Planning Authority, including photographs of the solar array, installer confirmation, an energy generation statement for the period that the solar PV array has been installed, and a Microgeneration Certification Scheme certificate.

Reason: To ensure the development reduces its impact on climate change by reducing carbon emissions on site in compliance with the Energy Hierarchy, and in line with London Plan (2021) Policy SI2, and Local Plan (2017) Policies SP4 and DM22.

Overheating 
Prior to above ground construction, a statement shall be submitted to and approved by the Local Planning Authority to demonstrate how the overheating risk has been minimised and mitigated on site in line with the London Plan Cooling Hierarchy. Details and specification of the mitigation measures shall be provided in support of this statement.

Reason: In the interest of reducing the impacts of climate change and mitigation of overheating risk, in accordance with London Plan (2021) Policy SI4, and Local Plan (2017) Policies SP4 and DM21.

image1.png
Photovoltaic Array

Number of Panels 9
Approximate Area per Panel 164
Approximate Surface Area Required 1476
Panel Output (kWp) 045

Total Output (kWp) 4.050
Total Output (kWhyear) 3,604.50
SAP 2012 Carbon Factor (kg.CO2 /kWh) 0156
CO2 Offset (kg.CO2 iyear) 562.3
‘Approximate Install Cost (€)' £4,500.00
Yearly Savings (£)2 £829.03
Payback (Years) 542
Lifespan Profit (25 Years) (€) £20,725.75
E::rg),/\ r(:g)sel Per Year (%) — 9,105kWhiyr (Reg 39.58%

1. Approximate Market Cost
2. Based on £0.24Wh




