## GRAPHS
|  |  | PASS | FAIL
PASSIVE | DSY1 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 40 | 0
| DSY2 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 2 | 38
| DSY3 | TM52 CRITERIA 1 | 60 | 0
|  | 26°C (BED ONLY) | 3 | 37
PASSIVE BRISE | DSY1 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 40 | 0
| DSY2 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 3 | 37
| DSY3 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 5 | 35
PASSIVE BLINDS | DSY1 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 40 | 0
| DSY2 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 2 | 38
| DSY3 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 3 | 37
PASSIVE 1.5ACH | DSY1 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 40 | 0
| DSY2 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 2 | 38
| DSY3 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 3 | 37
PASSIVE 1.5kW | DSY1 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 40 | 0
| DSY2 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 40 | 0
| DSY3 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 40 | 0
PASSIVE | DSY1 | TM52 CRITERIA 1 | 0.017187 | %
|  | 26°C (BED ONLY) | 14.475 | annual hrs
| DSY2 | TM52 CRITERIA 1 | 0.51875 | %
|  | 26°C (BED ONLY) | 47.525 | annual hrs
| DSY3 | TM52 CRITERIA 1 | 0.43594 | %
|  | 26°C (BED ONLY) | 40.575 | annual hrs
PASSIVE BRISE | DSY1 | TM52 CRITERIA 1 | 0 | %
|  | 26°C (BED ONLY) | 13.475 | annual hrs
| DSY2 | TM52 CRITERIA 1 | 0.2875 | % | `
|  | 26°C (BED ONLY) | 45 | annual hrs
| DSY3 | TM52 CRITERIA 1 | 0.225 | %
|  | 26°C (BED ONLY) | 38.275 | annual hrs
PASSIVE BLINDS | DSY1 | TM52 CRITERIA 1 | 0.017187 | %
|  | 26°C (BED ONLY) | 14.475 | annual hrs
| DSY2 | TM52 CRITERIA 1 | 0.51875 | %
|  | 26°C (BED ONLY) | 47.525 | annual hrs
| DSY3 | TM52 CRITERIA 1 | 0.43594 | %
|  | 26°C (BED ONLY) | 40.575 | annual hrs
PASSIVE 1.5ACH | DSY1 | TM52 CRITERIA 1 | 0.053125 | %
|  | 26°C (BED ONLY) | 14.15 | annual hrs
| DSY2 | TM52 CRITERIA 1 | 0.79844 | %
|  | 26°C (BED ONLY) | 45.175 | annual hrs
| DSY3 | TM52 CRITERIA 1 | 0.67969 | %
|  | 26°C (BED ONLY) | 39.55 | annual hrs
PASSIVE 1.5kW | DSY1 | TM52 CRITERIA 1 | 0 | %
|  | 26°C (BED ONLY) | 0 | annual hrs
| DSY2 | TM52 CRITERIA 1 | 0 | %
|  | 26°C (BED ONLY) | 0 | annual hrs
| DSY3 | TM52 CRITERIA 1 | 0 | %
|  | 26°C (BED ONLY) | 0 | annual hrs
|  |  | PASS | FAIL
PASSIVE 1.5kW | 2050DSY1 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 40 | 0
| 2050DSY2 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 40 | 0
| 2050DSY3 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 40 | 0
PASSIVE 1.5kW | 2080DSY1 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 40 | 0
| 2080DSY2 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 40 | 0
| 2080DSY3 | TM52 CRITERIA 1 | 64 | 0
|  | 26°C (BED ONLY) | 40 | 0

## PASSIVE DSY1_TM52
Overall | [8 empty] | Operative temperature (TM 52/CIBSE) (°C) - hours in range |  |  | Operative temperature (TM 52/CIBSE) (°C) - hours in range
Passed: | 64 rooms: | [5 empty] | File | Location | > 26.10 | File | Location | > 26.10
Failed: | 0 rooms: | [5 empty] | PASSIVE DSY1.aps | 001/1B2P/BED | 7 | PASSIVE DSY1.aps | 001/1B2P/BED | 6 | 13
Unoccupied: | 0 rooms: | [5 empty] | PASSIVE DSY1.aps | 002/1B2P/BED | 7 | PASSIVE DSY1.aps | 002/1B2P/BED | 5 | 12
[7 empty] | PASSIVE DSY1.aps | 003/3B5P/BED1 | 8 | PASSIVE DSY1.aps | 003/3B5P/BED1 | 7 | 15
Data: | [6 empty] | PASSIVE DSY1.aps | 003/3B5P/BED2 | 9 | PASSIVE DSY1.aps | 003/3B5P/BED2 | 6 | 15
Building category: | Category II (new builds.) | [5 empty] | PASSIVE DSY1.aps | 003/3B5P/BED3 | 12 | PASSIVE DSY1.aps | 003/3B5P/BED3 | 8 | 20
Weather file: | London_LWC_DSY1_2020High50.epw | [5 empty] | PASSIVE DSY1.aps | 004/3B5P/BED1 | 9 | PASSIVE DSY1.aps | 004/3B5P/BED1 | 8 | 17
Days data= | 365 | 2021-01-01 | 2021-12-31 |  |  |  | PASSIVE DSY1.aps | 004/3B5P/BED2 | 10 | PASSIVE DSY1.aps | 004/3B5P/BED2 | 8 | 18
Days (summer)= | 153 | 2021-05-01 | 2021-09-30 |  |  |  | PASSIVE DSY1.aps | 004/3B5P/BED3 | 12 | PASSIVE DSY1.aps | 004/3B5P/BED3 | 8 | 20
Data OK? | OK | Full summer |  |  |  |  | PASSIVE DSY1.aps | 005/3B5P/BED1 | 9 | PASSIVE DSY1.aps | 005/3B5P/BED1 | 8 | 17
[7 empty] | PASSIVE DSY1.aps | 005/3B5P/BED2 | 10 | PASSIVE DSY1.aps | 005/3B5P/BED2 | 8 | 18
Occupancy: | [6 empty] | PASSIVE DSY1.aps | 005/3B5P/BED3 | 12 | PASSIVE DSY1.aps | 005/3B5P/BED3 | 8 | 20
Note: | This report assesses occupied periods only. Please be aware that TM52 should be conducted for occupied and/or “available hours”. | [5 empty] | PASSIVE DSY1.aps | 006/3B5P/BED1 | 8 | PASSIVE DSY1.aps | 006/3B5P/BED1 | 7 | 15
| Use of educational NCM profiles may be seen as inappropriate due to prolonged unoccupied periods during summer months. | [5 empty] | PASSIVE DSY1.aps | 006/3B5P/BED2 | 9 | PASSIVE DSY1.aps | 006/3B5P/BED2 | 6 | 15
| See Section 6.1.2 (a) of TM52 for further information. | [5 empty] | PASSIVE DSY1.aps | 006/3B5P/BED3 | 12 | PASSIVE DSY1.aps | 006/3B5P/BED3 | 8 | 20
[7 empty] | PASSIVE DSY1.aps | 007/1B2P/BED | 7 | PASSIVE DSY1.aps | 007/1B2P/BED | 5 | 12
Passed: | 64 rooms: | [5 empty] | PASSIVE DSY1.aps | 008/1B2P/BED | 9 | PASSIVE DSY1.aps | 008/1B2P/BED | 8 | 17
Room Name | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing | PASS MARK | PASSIVE DSY1.aps | 009/4B6P/BED1 | 12 | PASSIVE DSY1.aps | 009/4B6P/BED1 | 7 | 19
001/1B2P/BED | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 009/4B6P/BED2 | 7 | PASSIVE DSY1.aps | 009/4B6P/BED2 | 2 | 9
001/1B2P/LDK | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 009/4B6P/BED3 | 8 | PASSIVE DSY1.aps | 009/4B6P/BED3 | 2 | 10
002/1B2P/BED | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 009/4B6P/BED4 | 12 | PASSIVE DSY1.aps | 009/4B6P/BED4 | 7 | 19
002/1B2P/LDK | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 010/4B6P/BED1 | 12 | PASSIVE DSY1.aps | 010/4B6P/BED1 | 7 | 19
003/3B5P/BED1 | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 010/4B6P/BED2 | 7 | PASSIVE DSY1.aps | 010/4B6P/BED2 | 3 | 10
003/3B5P/BED2 | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 010/4B6P/BED3 | 7 | PASSIVE DSY1.aps | 010/4B6P/BED3 | 3 | 10
003/3B5P/BED3 | 100 | 0.1 | 2 | 1 | - | 3 | PASSIVE DSY1.aps | 010/4B6P/BED4 | 12 | PASSIVE DSY1.aps | 010/4B6P/BED4 | 8 | 20
003/3B5P/DINKIT | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 011/2B4P/BED1 | 7 | PASSIVE DSY1.aps | 011/2B4P/BED1 | 4 | 11
003/3B5P/LIV | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 011/2B4P/BED2 | 7 | PASSIVE DSY1.aps | 011/2B4P/BED2 | 4 | 11
004/3B5P/BED1 | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 012/2B4P/BED1 | 7 | PASSIVE DSY1.aps | 012/2B4P/BED1 | 4 | 11
004/3B5P/BED2 | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 012/2B4P/BED2 | 8 | PASSIVE DSY1.aps | 012/2B4P/BED2 | 4 | 12
004/3B5P/BED3 | 100 | 0.2 | 6 | 1 | - | 3 | PASSIVE DSY1.aps | 013/2B4P/BED1 | 7 | PASSIVE DSY1.aps | 013/2B4P/BED1 | 4 | 11
004/3B5P/DINKIT | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 013/2B4P/BED2 | 8 | PASSIVE DSY1.aps | 013/2B4P/BED2 | 4 | 12
004/3B5P/LIV | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 014/2B4P/BED1 | 7 | PASSIVE DSY1.aps | 014/2B4P/BED1 | 5 | 12
005/3B5P/BED1 | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 014/2B4P/BED2 | 7 | PASSIVE DSY1.aps | 014/2B4P/BED2 | 4 | 11
005/3B5P/BED2 | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 015/2B4P/BED1 | 7 | PASSIVE DSY1.aps | 015/2B4P/BED1 | 6 | 13
005/3B5P/BED3 | 100 | 0.2 | 6 | 1 | - | 3 | PASSIVE DSY1.aps | 015/2B4P/BED2 | 8 | PASSIVE DSY1.aps | 015/2B4P/BED2 | 6 | 14
005/3B5P/DINKIT | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 016/2B4P/BED1 | 7 | PASSIVE DSY1.aps | 016/2B4P/BED1 | 5 | 12
005/3B5P/LIV | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 016/2B4P/BED2 | 8 | PASSIVE DSY1.aps | 016/2B4P/BED2 | 5 | 13
006/3B5P/BED1 | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 017/2B4P/BED1 | 8 | PASSIVE DSY1.aps | 017/2B4P/BED1 | 5 | 13
006/3B5P/BED2 | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 017/2B4P/BED2 | 8 | PASSIVE DSY1.aps | 017/2B4P/BED2 | 6 | 14
006/3B5P/BED3 | 100 | 0.1 | 2 | 1 | - | 3 | PASSIVE DSY1.aps | 018/2B4P/BED1 | 8 | PASSIVE DSY1.aps | 018/2B4P/BED1 | 6 | 14
006/3B5P/DINKIT | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | 018/2B4P/BED2 | 8 | PASSIVE DSY1.aps | 018/2B4P/BED2 | 7 | 15
006/3B5P/LIV | 100 | 0 | 0 | 0 | - | 3 | PASSIVE DSY1.aps | Total hours | 347 | PASSIVE DSY1.aps | Total hours | 232
007/1B2P/BED | 100 | 0 | 0 | 0 | - | 3
007/1B2P/LDK | 100 | 0 | 0 | 0 | - | 3
008/1B2P/BED | 100 | 0 | 0 | 0 | - | 3
008/1B2P/LDK | 100 | 0 | 0 | 0 | - | 3
009/4B6P/BED1 | 100 | 0.1 | 3 | 1 | - | 3
009/4B6P/BED2 | 100 | 0 | 0 | 0 | - | 3
009/4B6P/BED3 | 100 | 0 | 0 | 0 | - | 3
009/4B6P/BED4 | 100 | 0.1 | 5 | 1 | - | 3
009/4B6P/DINKIT | 100 | 0 | 0 | 0 | - | 3
009/4B6P/LIV | 100 | 0 | 0 | 0 | - | 3
010/4B6P/BED1 | 100 | 0.1 | 3 | 1 | - | 3
010/4B6P/BED2 | 100 | 0 | 0 | 0 | - | 3
010/4B6P/BED3 | 100 | 0 | 0 | 0 | - | 3
010/4B6P/BED4 | 100 | 0.2 | 6 | 1 | - | 3
010/4B6P/DINKIT | 100 | 0 | 0 | 0 | - | 3
010/4B6P/LIV | 100 | 0 | 0 | 0 | - | 3
011/2B4P/BED1 | 100 | 0 | 0 | 0 | - | 3
011/2B4P/BED2 | 100 | 0 | 0 | 0 | - | 3
011/2B4P/LDK | 100 | 0 | 0 | 0 | - | 3
012/2B4P/BED1 | 100 | 0 | 0 | 0 | - | 3
012/2B4P/BED2 | 100 | 0 | 0 | 0 | - | 3
012/2B4P/LDK | 100 | 0 | 0 | 0 | - | 3
013/2B4P/BED1 | 100 | 0 | 0 | 0 | - | 3
013/2B4P/BED2 | 100 | 0 | 0 | 0 | - | 3
013/2B4P/LDK | 100 | 0 | 0 | 0 | - | 3
014/2B4P/BED1 | 100 | 0 | 0 | 0 | - | 3
014/2B4P/BED2 | 100 | 0 | 0 | 0 | - | 3
014/2B4P/LDK | 100 | 0 | 0 | 0 | - | 3
015/2B4P/BED1 | 100 | 0 | 0 | 0 | - | 3
015/2B4P/BED2 | 100 | 0 | 0 | 0 | - | 3
015/2B4P/LDK | 100 | 0 | 0 | 0 | - | 3
016/2B4P/BED1 | 100 | 0 | 0 | 0 | - | 3
016/2B4P/BED2 | 100 | 0 | 0 | 0 | - | 3
016/2B4P/LDK | 100 | 0 | 0 | 0 | - | 3
017/2B4P/BED1 | 100 | 0 | 0 | 0 | - | 3
017/2B4P/BED2 | 100 | 0 | 0 | 0 | - | 3
017/2B4P/LDK | 100 | 0 | 0 | 0 | - | 3
018/2B4P/BED1 | 100 | 0 | 0 | 0 | - | 3
018/2B4P/BED2 | 100 | 0 | 0 | 0 | - | 3
018/2B4P/LDK | 100 | 0 | 0 | 0 | - | 3
Failed:
Room Name | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Unoccupied: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Note: | A TM 52 2013 analysis provides an assessment of comfort compliance based on bulk air modelling
i.e. each space is considered idealised and the air in the space perfectly mixed. The assessment does
not assess placement of space features e.g. windows & openings, airflow patterns or discomfort issues.
The user should assess these design aspects outside of the TM52 analysis.

## PASSIVE DSY2_TM52
Overall | [8 empty] | Operative temperature (TM 52/CIBSE) (°C) - hours in range |  |  | Operative temperature (TM 52/CIBSE) (°C) - hours in range
Passed: | 64 rooms: | [5 empty] | File | Location | > 26.10 | File | Location | > 26.10
Failed: | 0 rooms: | [5 empty] | PASSIVE DSY2.aps | 001/1B2P/BED | 18 | PASSIVE DSY2.aps | 001/1B2P/BED | 36 | 54
Unoccupied: | 0 rooms: | [5 empty] | PASSIVE DSY2.aps | 002/1B2P/BED | 17 | PASSIVE DSY2.aps | 002/1B2P/BED | 31 | 48
[7 empty] | PASSIVE DSY2.aps | 003/3B5P/BED1 | 17 | PASSIVE DSY2.aps | 003/3B5P/BED1 | 35 | 52
Data: | [6 empty] | PASSIVE DSY2.aps | 003/3B5P/BED2 | 19 | PASSIVE DSY2.aps | 003/3B5P/BED2 | 32 | 51
Building category: | Category II (new builds.) | [5 empty] | PASSIVE DSY2.aps | 003/3B5P/BED3 | 20 | PASSIVE DSY2.aps | 003/3B5P/BED3 | 31 | 51
Weather file: | London_LWC_DSY2_2020High50.epw | [5 empty] | PASSIVE DSY2.aps | 004/3B5P/BED1 | 19 | PASSIVE DSY2.aps | 004/3B5P/BED1 | 34 | 53
Days data= | 365 | 2021-01-01 | 2021-12-31 |  |  |  | PASSIVE DSY2.aps | 004/3B5P/BED2 | 21 | PASSIVE DSY2.aps | 004/3B5P/BED2 | 36 | 57
Days (summer)= | 153 | 2021-05-01 | 2021-09-30 |  |  |  | PASSIVE DSY2.aps | 004/3B5P/BED3 | 21 | PASSIVE DSY2.aps | 004/3B5P/BED3 | 32 | 53
Data OK? | OK | Full summer |  |  |  |  | PASSIVE DSY2.aps | 005/3B5P/BED1 | 19 | PASSIVE DSY2.aps | 005/3B5P/BED1 | 34 | 53
[7 empty] | PASSIVE DSY2.aps | 005/3B5P/BED2 | 21 | PASSIVE DSY2.aps | 005/3B5P/BED2 | 36 | 57
Occupancy: | [6 empty] | PASSIVE DSY2.aps | 005/3B5P/BED3 | 21 | PASSIVE DSY2.aps | 005/3B5P/BED3 | 32 | 53
Note: | This report assesses occupied periods only. Please be aware that TM52 should be conducted for occupied and/or “available hours”. | [5 empty] | PASSIVE DSY2.aps | 006/3B5P/BED1 | 17 | PASSIVE DSY2.aps | 006/3B5P/BED1 | 35 | 52
| Use of educational NCM profiles may be seen as inappropriate due to prolonged unoccupied periods during summer months. | [5 empty] | PASSIVE DSY2.aps | 006/3B5P/BED2 | 19 | PASSIVE DSY2.aps | 006/3B5P/BED2 | 33 | 52
| See Section 6.1.2 (a) of TM52 for further information. | [5 empty] | PASSIVE DSY2.aps | 006/3B5P/BED3 | 20 | PASSIVE DSY2.aps | 006/3B5P/BED3 | 31 | 51
[7 empty] | PASSIVE DSY2.aps | 007/1B2P/BED | 17 | PASSIVE DSY2.aps | 007/1B2P/BED | 31 | 48
Passed: | 64 rooms: | [5 empty] | PASSIVE DSY2.aps | 008/1B2P/BED | 18 | PASSIVE DSY2.aps | 008/1B2P/BED | 39 | 57
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing | PASSIVE DSY2.aps | 009/4B6P/BED1 | 20 | PASSIVE DSY2.aps | 009/4B6P/BED1 | 29 | 49
001/1B2P/BED | 2 | 100 | 0 | 0 | 0 | - | PASSIVE DSY2.aps | 009/4B6P/BED2 | 16 | PASSIVE DSY2.aps | 009/4B6P/BED2 | 15 | 31
001/1B2P/LDK | 0 | 100 | 0.4 | 7 | 1 | 2 | PASSIVE DSY2.aps | 009/4B6P/BED3 | 16 | PASSIVE DSY2.aps | 009/4B6P/BED3 | 19 | 35
002/1B2P/BED | 7 | 100 | 0 | 0 | 0 | - | PASSIVE DSY2.aps | 009/4B6P/BED4 | 20 | PASSIVE DSY2.aps | 009/4B6P/BED4 | 32 | 52
002/1B2P/LDK | 5 | 100 | 0.1 | 1 | 1 | - | PASSIVE DSY2.aps | 010/4B6P/BED1 | 20 | PASSIVE DSY2.aps | 010/4B6P/BED1 | 32 | 52
003/3B5P/BED1 | 0000005A | 100 | 0.2 | 7 | 1 | 2 | PASSIVE DSY2.aps | 010/4B6P/BED2 | 17 | PASSIVE DSY2.aps | 010/4B6P/BED2 | 16 | 33
003/3B5P/BED2 | 0000005B | 100 | 0.7 | 16 | 2 | 2 | PASSIVE DSY2.aps | 010/4B6P/BED3 | 17 | PASSIVE DSY2.aps | 010/4B6P/BED3 | 14 | 31
003/3B5P/BED3 | 0000005C | 100 | 1.1 | 24 | 3 | 2 | PASSIVE DSY2.aps | 010/4B6P/BED4 | 20 | PASSIVE DSY2.aps | 010/4B6P/BED4 | 32 | 52
003/3B5P/DINKIT | 0000000D | 100 | 0.7 | 10 | 2 | 2 | PASSIVE DSY2.aps | 011/2B4P/BED1 | 16 | PASSIVE DSY2.aps | 011/2B4P/BED1 | 25 | 41
003/3B5P/LIV | 0000000C | 100 | 0.8 | 12 | 2 | 2 | PASSIVE DSY2.aps | 011/2B4P/BED2 | 17 | PASSIVE DSY2.aps | 011/2B4P/BED2 | 25 | 42
004/3B5P/BED1 | 62 | 100 | 0.6 | 14 | 2 | 2 | PASSIVE DSY2.aps | 012/2B4P/BED1 | 16 | PASSIVE DSY2.aps | 012/2B4P/BED1 | 25 | 41
004/3B5P/BED2 | 63 | 100 | 1 | 21 | 3 | 2 | PASSIVE DSY2.aps | 012/2B4P/BED2 | 17 | PASSIVE DSY2.aps | 012/2B4P/BED2 | 22 | 39
004/3B5P/BED3 | 64 | 100 | 1.1 | 26 | 4 | 2 | PASSIVE DSY2.aps | 013/2B4P/BED1 | 17 | PASSIVE DSY2.aps | 013/2B4P/BED1 | 24 | 41
004/3B5P/DINKIT | 19 | 100 | 1.2 | 14 | 2 | 2 | PASSIVE DSY2.aps | 013/2B4P/BED2 | 17 | PASSIVE DSY2.aps | 013/2B4P/BED2 | 22 | 39
004/3B5P/LIV | 18 | 100 | 1.6 | 18 | 3 | 2 | PASSIVE DSY2.aps | 014/2B4P/BED1 | 17 | PASSIVE DSY2.aps | 014/2B4P/BED1 | 29 | 46
005/3B5P/BED1 | 69 | 100 | 0.6 | 14 | 2 | 2 | PASSIVE DSY2.aps | 014/2B4P/BED2 | 17 | PASSIVE DSY2.aps | 014/2B4P/BED2 | 28 | 45
005/3B5P/BED2 | 0000006A | 100 | 1 | 21 | 3 | 2 | PASSIVE DSY2.aps | 015/2B4P/BED1 | 17 | PASSIVE DSY2.aps | 015/2B4P/BED1 | 32 | 49
005/3B5P/BED3 | 0000006B | 100 | 1.1 | 26 | 4 | 2 | PASSIVE DSY2.aps | 015/2B4P/BED2 | 17 | PASSIVE DSY2.aps | 015/2B4P/BED2 | 32 | 49
005/3B5P/DINKIT | 0000001A | 100 | 1.2 | 14 | 2 | 2 | PASSIVE DSY2.aps | 016/2B4P/BED1 | 17 | PASSIVE DSY2.aps | 016/2B4P/BED1 | 30 | 47
005/3B5P/LIV | 0000001B | 100 | 1.6 | 18 | 3 | 2 | PASSIVE DSY2.aps | 016/2B4P/BED2 | 17 | PASSIVE DSY2.aps | 016/2B4P/BED2 | 30 | 47
006/3B5P/BED1 | 71 | 100 | 0.2 | 6 | 1 | - | PASSIVE DSY2.aps | 017/2B4P/BED1 | 17 | PASSIVE DSY2.aps | 017/2B4P/BED1 | 31 | 48
006/3B5P/BED2 | 70 | 100 | 0.6 | 14 | 2 | 2 | PASSIVE DSY2.aps | 017/2B4P/BED2 | 17 | PASSIVE DSY2.aps | 017/2B4P/BED2 | 31 | 48
006/3B5P/BED3 | 0000006F | 100 | 1 | 22 | 3 | 2 | PASSIVE DSY2.aps | 018/2B4P/BED1 | 18 | PASSIVE DSY2.aps | 018/2B4P/BED1 | 33 | 51
006/3B5P/DINKIT | 27 | 100 | 0.6 | 10 | 2 | 2 | PASSIVE DSY2.aps | 018/2B4P/BED2 | 18 | PASSIVE DSY2.aps | 018/2B4P/BED2 | 33 | 51
006/3B5P/LIV | 26 | 100 | 0.8 | 12 | 2 | 2 | PASSIVE DSY2.aps | Total hours | 722 | PASSIVE DSY2.aps | Total hours | 1179
007/1B2P/BED | 29 | 100 | 0 | 0 | 0 | -
007/1B2P/LDK | 28 | 100 | 0.1 | 1 | 1 | -
008/1B2P/BED | 31 | 100 | 0.1 | 2 | 1 | -
008/1B2P/LDK | 30 | 100 | 0.6 | 11 | 2 | 2
009/4B6P/BED1 | 76 | 100 | 0.9 | 20 | 3 | 2
009/4B6P/BED2 | 77 | 100 | 0.3 | 10 | 2 | 2
009/4B6P/BED3 | 78 | 100 | 0.6 | 14 | 2 | 2
009/4B6P/BED4 | 79 | 100 | 1 | 23 | 4 | 2
009/4B6P/DINKIT | 0000003D | 100 | 0.4 | 6 | 1 | -
009/4B6P/LIV | 0000003C | 100 | 1.4 | 17 | 3 | 2
010/4B6P/BED1 | 1000026 | 100 | 0.9 | 20 | 3 | 2
010/4B6P/BED2 | 1000027 | 100 | 0.3 | 13 | 2 | 2
010/4B6P/BED3 | 1000028 | 100 | 0.6 | 15 | 2 | 2
010/4B6P/BED4 | 1000029 | 100 | 1 | 25 | 4 | 2
010/4B6P/DINKIT | 1000006 | 100 | 0.7 | 15 | 2 | 2
010/4B6P/LIV | 1000005 | 100 | 1.6 | 21 | 3 | 2
011/2B4P/BED1 | 1000009 | 100 | 0 | 0 | 0 | -
011/2B4P/BED2 | 0100000A | 100 | 0 | 0 | 0 | -
011/2B4P/LDK | 1000008 | 100 | 0.2 | 4 | 1 | -
012/2B4P/BED1 | 1000011 | 100 | 0 | 0 | 0 | -
012/2B4P/BED2 | 1000012 | 100 | 0.1 | 2 | 1 | -
012/2B4P/LDK | 1000010 | 100 | 0.1 | 2 | 1 | -
013/2B4P/BED1 | 1000017 | 100 | 0 | 0 | 0 | -
013/2B4P/BED2 | 1000018 | 100 | 0.1 | 2 | 1 | -
013/2B4P/LDK | 1000016 | 100 | 0.1 | 2 | 1 | -
014/2B4P/BED1 | 1000020 | 100 | 0 | 0 | 0 | -
014/2B4P/BED2 | 1000021 | 100 | 0.1 | 2 | 1 | -
014/2B4P/LDK | 0100001F | 100 | 0.1 | 2 | 1 | -
015/2B4P/BED1 | 0100002D | 100 | 0 | 0 | 0 | -
015/2B4P/BED2 | 0100002E | 100 | 0.2 | 8 | 1 | 2
015/2B4P/LDK | 1000031 | 100 | 0.7 | 14 | 2 | 2
016/2B4P/BED1 | 1000034 | 100 | 0 | 0 | 0 | -
016/2B4P/BED2 | 1000035 | 100 | 0.1 | 5 | 1 | -
016/2B4P/LDK | 1000038 | 100 | 0.6 | 12 | 2 | 2
017/2B4P/BED1 | 0100003B | 100 | 0 | 1 | 1 | -
017/2B4P/BED2 | 0100003C | 100 | 0.2 | 6 | 1 | -
017/2B4P/LDK | 0100003A | 100 | 0.7 | 12 | 2 | 2
018/2B4P/BED1 | 1000044 | 100 | 0.1 | 4 | 1 | -
018/2B4P/BED2 | 1000045 | 100 | 0.2 | 9 | 2 | 2
018/2B4P/LDK | 1000043 | 100 | 0.9 | 14 | 2 | 2
Failed: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Unoccupied: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Note: | A TM 52 2013 analysis provides an assessment of comfort compliance based on bulk air modelling
i.e. each space is considered idealised and the air in the space perfectly mixed. The assessment does
not assess placement of space features e.g. windows & openings, airflow patterns or discomfort issues.
The user should assess these design aspects outside of the TM52 analysis.

## PASSIVE DSY3_TM52
Overall | [8 empty] | Operative temperature (TM 52/CIBSE) (°C) - hours in range |  |  | Operative temperature (TM 52/CIBSE) (°C) - hours in range
Passed: | 64 rooms: | [5 empty] | File | Location | > 26.10 | File | Location | > 26.10
Failed: | 0 rooms: | [5 empty] | PASSIVE DSY3.aps | 001/1B2P/BED | 21 | PASSIVE DSY3.aps | 001/1B2P/BED | 22 | 43
Unoccupied: | 0 rooms: | [5 empty] | PASSIVE DSY3.aps | 002/1B2P/BED | 21 | PASSIVE DSY3.aps | 002/1B2P/BED | 18 | 39
[7 empty] | PASSIVE DSY3.aps | 003/3B5P/BED1 | 22 | PASSIVE DSY3.aps | 003/3B5P/BED1 | 22 | 44
Data: | [6 empty] | PASSIVE DSY3.aps | 003/3B5P/BED2 | 21 | PASSIVE DSY3.aps | 003/3B5P/BED2 | 22 | 43
Building category: | Category II (new builds.) | [5 empty] | PASSIVE DSY3.aps | 003/3B5P/BED3 | 22 | PASSIVE DSY3.aps | 003/3B5P/BED3 | 24 | 46
Weather file: | London_LWC_DSY3_2020High50.epw | [5 empty] | PASSIVE DSY3.aps | 004/3B5P/BED1 | 22 | PASSIVE DSY3.aps | 004/3B5P/BED1 | 23 | 45
Days data= | 365 | 2021-01-01 | 2021-12-31 |  |  |  | PASSIVE DSY3.aps | 004/3B5P/BED2 | 26 | PASSIVE DSY3.aps | 004/3B5P/BED2 | 25 | 51
Days (summer)= | 153 | 2021-05-01 | 2021-09-30 |  |  |  | PASSIVE DSY3.aps | 004/3B5P/BED3 | 22 | PASSIVE DSY3.aps | 004/3B5P/BED3 | 24 | 46
Data OK? | OK | Full summer |  |  |  |  | PASSIVE DSY3.aps | 005/3B5P/BED1 | 22 | PASSIVE DSY3.aps | 005/3B5P/BED1 | 23 | 45
[7 empty] | PASSIVE DSY3.aps | 005/3B5P/BED2 | 26 | PASSIVE DSY3.aps | 005/3B5P/BED2 | 25 | 51
Occupancy: | [6 empty] | PASSIVE DSY3.aps | 005/3B5P/BED3 | 22 | PASSIVE DSY3.aps | 005/3B5P/BED3 | 24 | 46
Note: | This report assesses occupied periods only. Please be aware that TM52 should be conducted for occupied and/or “available hours”. | [5 empty] | PASSIVE DSY3.aps | 006/3B5P/BED1 | 22 | PASSIVE DSY3.aps | 006/3B5P/BED1 | 22 | 44
| Use of educational NCM profiles may be seen as inappropriate due to prolonged unoccupied periods during summer months. | [5 empty] | PASSIVE DSY3.aps | 006/3B5P/BED2 | 22 | PASSIVE DSY3.aps | 006/3B5P/BED2 | 21 | 43
| See Section 6.1.2 (a) of TM52 for further information. | [5 empty] | PASSIVE DSY3.aps | 006/3B5P/BED3 | 22 | PASSIVE DSY3.aps | 006/3B5P/BED3 | 24 | 46
[7 empty] | PASSIVE DSY3.aps | 007/1B2P/BED | 21 | PASSIVE DSY3.aps | 007/1B2P/BED | 18 | 39
Passed: | 64 rooms: | [5 empty] | PASSIVE DSY3.aps | 008/1B2P/BED | 23 | PASSIVE DSY3.aps | 008/1B2P/BED | 24 | 47
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing | PASSIVE DSY3.aps | 009/4B6P/BED1 | 22 | PASSIVE DSY3.aps | 009/4B6P/BED1 | 20 | 42
001/1B2P/BED | 2 | 100 | 0 | 0 | 0 | - | PASSIVE DSY3.aps | 009/4B6P/BED2 | 18 | PASSIVE DSY3.aps | 009/4B6P/BED2 | 11 | 29
001/1B2P/LDK | 0 | 100 | 0 | 0 | 0 | - | PASSIVE DSY3.aps | 009/4B6P/BED3 | 19 | PASSIVE DSY3.aps | 009/4B6P/BED3 | 15 | 34
002/1B2P/BED | 7 | 100 | 0 | 0 | 0 | - | PASSIVE DSY3.aps | 009/4B6P/BED4 | 23 | PASSIVE DSY3.aps | 009/4B6P/BED4 | 23 | 46
002/1B2P/LDK | 5 | 100 | 0 | 0 | 0 | - | PASSIVE DSY3.aps | 010/4B6P/BED1 | 22 | PASSIVE DSY3.aps | 010/4B6P/BED1 | 22 | 44
003/3B5P/BED1 | 0000005A | 100 | 0.1 | 5 | 1 | - | PASSIVE DSY3.aps | 010/4B6P/BED2 | 18 | PASSIVE DSY3.aps | 010/4B6P/BED2 | 13 | 31
003/3B5P/BED2 | 0000005B | 100 | 0.7 | 9 | 1 | 2 | PASSIVE DSY3.aps | 010/4B6P/BED3 | 17 | PASSIVE DSY3.aps | 010/4B6P/BED3 | 10 | 27
003/3B5P/BED3 | 0000005C | 100 | 1 | 18 | 2 | 2 | PASSIVE DSY3.aps | 010/4B6P/BED4 | 24 | PASSIVE DSY3.aps | 010/4B6P/BED4 | 24 | 48
003/3B5P/DINKIT | 0000000D | 100 | 0.3 | 2 | 1 | - | PASSIVE DSY3.aps | 011/2B4P/BED1 | 18 | PASSIVE DSY3.aps | 011/2B4P/BED1 | 15 | 33
003/3B5P/LIV | 0000000C | 100 | 0.6 | 6 | 1 | - | PASSIVE DSY3.aps | 011/2B4P/BED2 | 19 | PASSIVE DSY3.aps | 011/2B4P/BED2 | 16 | 35
004/3B5P/BED1 | 62 | 100 | 0.7 | 9 | 1 | 2 | PASSIVE DSY3.aps | 012/2B4P/BED1 | 18 | PASSIVE DSY3.aps | 012/2B4P/BED1 | 16 | 34
004/3B5P/BED2 | 63 | 100 | 1 | 14 | 2 | 2 | PASSIVE DSY3.aps | 012/2B4P/BED2 | 19 | PASSIVE DSY3.aps | 012/2B4P/BED2 | 16 | 35
004/3B5P/BED3 | 64 | 100 | 1.2 | 20 | 2 | 2 | PASSIVE DSY3.aps | 013/2B4P/BED1 | 18 | PASSIVE DSY3.aps | 013/2B4P/BED1 | 16 | 34
004/3B5P/DINKIT | 19 | 100 | 0.7 | 6 | 1 | - | PASSIVE DSY3.aps | 013/2B4P/BED2 | 20 | PASSIVE DSY3.aps | 013/2B4P/BED2 | 16 | 36
004/3B5P/LIV | 18 | 100 | 1.3 | 10 | 2 | 2 | PASSIVE DSY3.aps | 014/2B4P/BED1 | 20 | PASSIVE DSY3.aps | 014/2B4P/BED1 | 17 | 37
005/3B5P/BED1 | 69 | 100 | 0.7 | 9 | 1 | 2 | PASSIVE DSY3.aps | 014/2B4P/BED2 | 20 | PASSIVE DSY3.aps | 014/2B4P/BED2 | 16 | 36
005/3B5P/BED2 | 0000006A | 100 | 1 | 14 | 2 | 2 | PASSIVE DSY3.aps | 015/2B4P/BED1 | 22 | PASSIVE DSY3.aps | 015/2B4P/BED1 | 18 | 40
005/3B5P/BED3 | 0000006B | 100 | 1.2 | 20 | 2 | 2 | PASSIVE DSY3.aps | 015/2B4P/BED2 | 22 | PASSIVE DSY3.aps | 015/2B4P/BED2 | 19 | 41
005/3B5P/DINKIT | 0000001A | 100 | 0.7 | 6 | 1 | - | PASSIVE DSY3.aps | 016/2B4P/BED1 | 21 | PASSIVE DSY3.aps | 016/2B4P/BED1 | 18 | 39
005/3B5P/LIV | 0000001B | 100 | 1.3 | 10 | 2 | 2 | PASSIVE DSY3.aps | 016/2B4P/BED2 | 20 | PASSIVE DSY3.aps | 016/2B4P/BED2 | 19 | 39
006/3B5P/BED1 | 71 | 100 | 0.1 | 5 | 1 | - | PASSIVE DSY3.aps | 017/2B4P/BED1 | 22 | PASSIVE DSY3.aps | 017/2B4P/BED1 | 18 | 40
006/3B5P/BED2 | 70 | 100 | 0.6 | 8 | 1 | 2 | PASSIVE DSY3.aps | 017/2B4P/BED2 | 21 | PASSIVE DSY3.aps | 017/2B4P/BED2 | 19 | 40
006/3B5P/BED3 | 0000006F | 100 | 1 | 18 | 2 | 2 | PASSIVE DSY3.aps | 018/2B4P/BED1 | 22 | PASSIVE DSY3.aps | 018/2B4P/BED1 | 20 | 42
006/3B5P/DINKIT | 27 | 100 | 0.2 | 2 | 1 | - | PASSIVE DSY3.aps | 018/2B4P/BED2 | 22 | PASSIVE DSY3.aps | 018/2B4P/BED2 | 21 | 43
006/3B5P/LIV | 26 | 100 | 0.6 | 6 | 1 | - | PASSIVE DSY3.aps | Total hours | 844 | PASSIVE DSY3.aps | Total hours | 779
007/1B2P/BED | 29 | 100 | 0 | 0 | 0 | -
007/1B2P/LDK | 28 | 100 | 0 | 0 | 0 | -
008/1B2P/BED | 31 | 100 | 0 | 0 | 0 | -
008/1B2P/LDK | 30 | 100 | 0.2 | 2 | 1 | -
009/4B6P/BED1 | 76 | 100 | 1 | 18 | 2 | 2
009/4B6P/BED2 | 77 | 100 | 0.4 | 6 | 1 | -
009/4B6P/BED3 | 78 | 100 | 0.7 | 9 | 1 | 2
009/4B6P/BED4 | 79 | 100 | 1.1 | 19 | 2 | 2
009/4B6P/DINKIT | 0000003D | 100 | 0.3 | 2 | 1 | -
009/4B6P/LIV | 0000003C | 100 | 1.2 | 8 | 1 | 2
010/4B6P/BED1 | 1000026 | 100 | 1 | 18 | 2 | 2
010/4B6P/BED2 | 1000027 | 100 | 0.5 | 8 | 1 | 2
010/4B6P/BED3 | 1000028 | 100 | 0.8 | 9 | 1 | 2
010/4B6P/BED4 | 1000029 | 100 | 1.2 | 19 | 2 | 2
010/4B6P/DINKIT | 1000006 | 100 | 1 | 7 | 1 | 2
010/4B6P/LIV | 1000005 | 100 | 1.6 | 14 | 2 | 2
011/2B4P/BED1 | 1000009 | 100 | 0 | 0 | 0 | -
011/2B4P/BED2 | 0100000A | 100 | 0 | 0 | 0 | -
011/2B4P/LDK | 1000008 | 100 | 0 | 0 | 0 | -
012/2B4P/BED1 | 1000011 | 100 | 0 | 0 | 0 | -
012/2B4P/BED2 | 1000012 | 100 | 0 | 0 | 0 | -
012/2B4P/LDK | 1000010 | 100 | 0 | 0 | 0 | -
013/2B4P/BED1 | 1000017 | 100 | 0 | 0 | 0 | -
013/2B4P/BED2 | 1000018 | 100 | 0 | 0 | 0 | -
013/2B4P/LDK | 1000016 | 100 | 0 | 0 | 0 | -
014/2B4P/BED1 | 1000020 | 100 | 0 | 0 | 0 | -
014/2B4P/BED2 | 1000021 | 100 | 0 | 0 | 0 | -
014/2B4P/LDK | 0100001F | 100 | 0 | 0 | 0 | -
015/2B4P/BED1 | 0100002D | 100 | 0 | 0 | 0 | -
015/2B4P/BED2 | 0100002E | 100 | 0 | 0 | 0 | -
015/2B4P/LDK | 1000031 | 100 | 0.3 | 2 | 1 | -
016/2B4P/BED1 | 1000034 | 100 | 0 | 0 | 0 | -
016/2B4P/BED2 | 1000035 | 100 | 0 | 0 | 0 | -
016/2B4P/LDK | 1000038 | 100 | 0.3 | 2 | 1 | -
017/2B4P/BED1 | 0100003B | 100 | 0 | 0 | 0 | -
017/2B4P/BED2 | 0100003C | 100 | 0 | 0 | 0 | -
017/2B4P/LDK | 0100003A | 100 | 0.6 | 4 | 1 | -
018/2B4P/BED1 | 1000044 | 100 | 0 | 0 | 0 | -
018/2B4P/BED2 | 1000045 | 100 | 0 | 0 | 0 | -
018/2B4P/LDK | 1000043 | 100 | 0.7 | 5 | 1 | -
Failed: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Unoccupied: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Note: | A TM 52 2013 analysis provides an assessment of comfort compliance based on bulk air modelling
i.e. each space is considered idealised and the air in the space perfectly mixed. The assessment does
not assess placement of space features e.g. windows & openings, airflow patterns or discomfort issues.
The user should assess these design aspects outside of the TM52 analysis.

## PASSIVE BRISE DSY1_TM52
Overall | [8 empty] | Operative temperature (TM 52/CIBSE) (°C) - hours in range |  |  | Operative temperature (TM 52/CIBSE) (°C) - hours in range
Passed: | 64 rooms: | [5 empty] | File | Location | > 26.10 | File | Location | > 26.10
Failed: | 0 rooms: | [5 empty] | PASSIVE BRISE DSY1.aps | 001/1B2P/BED | 7 | PASSIVE BRISE DSY1.aps | 001/1B2P/BED | 6 | 13
Unoccupied: | 0 rooms: | [5 empty] | PASSIVE BRISE DSY1.aps | 002/1B2P/BED | 7 | PASSIVE BRISE DSY1.aps | 002/1B2P/BED | 4 | 11
[7 empty] | PASSIVE BRISE DSY1.aps | 003/3B5P/BED1 | 8 | PASSIVE BRISE DSY1.aps | 003/3B5P/BED1 | 6 | 14
Data: | [6 empty] | PASSIVE BRISE DSY1.aps | 003/3B5P/BED2 | 8 | PASSIVE BRISE DSY1.aps | 003/3B5P/BED2 | 6 | 14
Building category: | Category II (new builds.) | [5 empty] | PASSIVE BRISE DSY1.aps | 003/3B5P/BED3 | 11 | PASSIVE BRISE DSY1.aps | 003/3B5P/BED3 | 7 | 18
Weather file: | London_LWC_DSY1_2020High50.epw | [5 empty] | PASSIVE BRISE DSY1.aps | 004/3B5P/BED1 | 9 | PASSIVE BRISE DSY1.aps | 004/3B5P/BED1 | 7 | 16
Days data= | 365 | 2021-01-01 | 2021-12-31 |  |  |  | PASSIVE BRISE DSY1.aps | 004/3B5P/BED2 | 9 | PASSIVE BRISE DSY1.aps | 004/3B5P/BED2 | 8 | 17
Days (summer)= | 153 | 2021-05-01 | 2021-09-30 |  |  |  | PASSIVE BRISE DSY1.aps | 004/3B5P/BED3 | 12 | PASSIVE BRISE DSY1.aps | 004/3B5P/BED3 | 7 | 19
Data OK? | OK | Full summer |  |  |  |  | PASSIVE BRISE DSY1.aps | 005/3B5P/BED1 | 9 | PASSIVE BRISE DSY1.aps | 005/3B5P/BED1 | 7 | 16
[7 empty] | PASSIVE BRISE DSY1.aps | 005/3B5P/BED2 | 9 | PASSIVE BRISE DSY1.aps | 005/3B5P/BED2 | 8 | 17
Occupancy: | [6 empty] | PASSIVE BRISE DSY1.aps | 005/3B5P/BED3 | 12 | PASSIVE BRISE DSY1.aps | 005/3B5P/BED3 | 7 | 19
Note: | This report assesses occupied periods only. Please be aware that TM52 should be conducted for occupied and/or “available hours”. | [5 empty] | PASSIVE BRISE DSY1.aps | 006/3B5P/BED1 | 8 | PASSIVE BRISE DSY1.aps | 006/3B5P/BED1 | 6 | 14
| Use of educational NCM profiles may be seen as inappropriate due to prolonged unoccupied periods during summer months. | [5 empty] | PASSIVE BRISE DSY1.aps | 006/3B5P/BED2 | 8 | PASSIVE BRISE DSY1.aps | 006/3B5P/BED2 | 6 | 14
| See Section 6.1.2 (a) of TM52 for further information. | [5 empty] | PASSIVE BRISE DSY1.aps | 006/3B5P/BED3 | 11 | PASSIVE BRISE DSY1.aps | 006/3B5P/BED3 | 7 | 18
[7 empty] | PASSIVE BRISE DSY1.aps | 007/1B2P/BED | 7 | PASSIVE BRISE DSY1.aps | 007/1B2P/BED | 4 | 11
Passed: | 64 rooms: | [5 empty] | PASSIVE BRISE DSY1.aps | 008/1B2P/BED | 8 | PASSIVE BRISE DSY1.aps | 008/1B2P/BED | 6 | 14
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing | PASSIVE BRISE DSY1.aps | 009/4B6P/BED1 | 11 | PASSIVE BRISE DSY1.aps | 009/4B6P/BED1 | 6 | 17
001/1B2P/BED | 2 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 009/4B6P/BED2 | 7 | PASSIVE BRISE DSY1.aps | 009/4B6P/BED2 | 2 | 9
001/1B2P/LDK | 0 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 009/4B6P/BED3 | 7 | PASSIVE BRISE DSY1.aps | 009/4B6P/BED3 | 2 | 9
002/1B2P/BED | 7 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 009/4B6P/BED4 | 11 | PASSIVE BRISE DSY1.aps | 009/4B6P/BED4 | 7 | 18
002/1B2P/LDK | 5 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 010/4B6P/BED1 | 12 | PASSIVE BRISE DSY1.aps | 010/4B6P/BED1 | 7 | 19
003/3B5P/BED1 | 0000005A | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 010/4B6P/BED2 | 7 | PASSIVE BRISE DSY1.aps | 010/4B6P/BED2 | 3 | 10
003/3B5P/BED2 | 0000005B | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 010/4B6P/BED3 | 7 | PASSIVE BRISE DSY1.aps | 010/4B6P/BED3 | 3 | 10
003/3B5P/BED3 | 0000005C | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 010/4B6P/BED4 | 11 | PASSIVE BRISE DSY1.aps | 010/4B6P/BED4 | 7 | 18
003/3B5P/DINKIT | 0000000D | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 011/2B4P/BED1 | 7 | PASSIVE BRISE DSY1.aps | 011/2B4P/BED1 | 3 | 10
003/3B5P/LIV | 0000000C | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 011/2B4P/BED2 | 7 | PASSIVE BRISE DSY1.aps | 011/2B4P/BED2 | 4 | 11
004/3B5P/BED1 | 62 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 012/2B4P/BED1 | 7 | PASSIVE BRISE DSY1.aps | 012/2B4P/BED1 | 4 | 11
004/3B5P/BED2 | 63 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 012/2B4P/BED2 | 8 | PASSIVE BRISE DSY1.aps | 012/2B4P/BED2 | 4 | 12
004/3B5P/BED3 | 64 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 013/2B4P/BED1 | 7 | PASSIVE BRISE DSY1.aps | 013/2B4P/BED1 | 4 | 11
004/3B5P/DINKIT | 19 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 013/2B4P/BED2 | 8 | PASSIVE BRISE DSY1.aps | 013/2B4P/BED2 | 4 | 12
004/3B5P/LIV | 18 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 014/2B4P/BED1 | 7 | PASSIVE BRISE DSY1.aps | 014/2B4P/BED1 | 4 | 11
005/3B5P/BED1 | 69 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 014/2B4P/BED2 | 7 | PASSIVE BRISE DSY1.aps | 014/2B4P/BED2 | 4 | 11
005/3B5P/BED2 | 0000006A | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 015/2B4P/BED1 | 7 | PASSIVE BRISE DSY1.aps | 015/2B4P/BED1 | 4 | 11
005/3B5P/BED3 | 0000006B | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 015/2B4P/BED2 | 7 | PASSIVE BRISE DSY1.aps | 015/2B4P/BED2 | 4 | 11
005/3B5P/DINKIT | 0000001A | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 016/2B4P/BED1 | 7 | PASSIVE BRISE DSY1.aps | 016/2B4P/BED1 | 4 | 11
005/3B5P/LIV | 0000001B | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 016/2B4P/BED2 | 8 | PASSIVE BRISE DSY1.aps | 016/2B4P/BED2 | 4 | 12
006/3B5P/BED1 | 71 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 017/2B4P/BED1 | 7 | PASSIVE BRISE DSY1.aps | 017/2B4P/BED1 | 5 | 12
006/3B5P/BED2 | 70 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 017/2B4P/BED2 | 8 | PASSIVE BRISE DSY1.aps | 017/2B4P/BED2 | 5 | 13
006/3B5P/BED3 | 0000006F | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 018/2B4P/BED1 | 7 | PASSIVE BRISE DSY1.aps | 018/2B4P/BED1 | 5 | 12
006/3B5P/DINKIT | 27 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | 018/2B4P/BED2 | 8 | PASSIVE BRISE DSY1.aps | 018/2B4P/BED2 | 5 | 13
006/3B5P/LIV | 26 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY1.aps | Total hours | 333 | PASSIVE BRISE DSY1.aps | Total hours | 206
007/1B2P/BED | 29 | 100 | 0 | 0 | 0 | -
007/1B2P/LDK | 28 | 100 | 0 | 0 | 0 | -
008/1B2P/BED | 31 | 100 | 0 | 0 | 0 | -
008/1B2P/LDK | 30 | 100 | 0 | 0 | 0 | -
009/4B6P/BED1 | 76 | 100 | 0 | 0 | 0 | -
009/4B6P/BED2 | 77 | 100 | 0 | 0 | 0 | -
009/4B6P/BED3 | 78 | 100 | 0 | 0 | 0 | -
009/4B6P/BED4 | 79 | 100 | 0 | 0 | 0 | -
009/4B6P/DINKIT | 0000003D | 100 | 0 | 0 | 0 | -
009/4B6P/LIV | 0000003C | 100 | 0 | 0 | 0 | -
010/4B6P/BED1 | 1000026 | 100 | 0 | 0 | 0 | -
010/4B6P/BED2 | 1000027 | 100 | 0 | 0 | 0 | -
010/4B6P/BED3 | 1000028 | 100 | 0 | 0 | 0 | -
010/4B6P/BED4 | 1000029 | 100 | 0 | 0 | 0 | -
010/4B6P/DINKIT | 1000006 | 100 | 0 | 0 | 0 | -
010/4B6P/LIV | 1000005 | 100 | 0 | 0 | 0 | -
011/2B4P/BED1 | 1000009 | 100 | 0 | 0 | 0 | -
011/2B4P/BED2 | 0100000A | 100 | 0 | 0 | 0 | -
011/2B4P/LDK | 1000008 | 100 | 0 | 0 | 0 | -
012/2B4P/BED1 | 1000011 | 100 | 0 | 0 | 0 | -
012/2B4P/BED2 | 1000012 | 100 | 0 | 0 | 0 | -
012/2B4P/LDK | 1000010 | 100 | 0 | 0 | 0 | -
013/2B4P/BED1 | 1000017 | 100 | 0 | 0 | 0 | -
013/2B4P/BED2 | 1000018 | 100 | 0 | 0 | 0 | -
013/2B4P/LDK | 1000016 | 100 | 0 | 0 | 0 | -
014/2B4P/BED1 | 1000020 | 100 | 0 | 0 | 0 | -
014/2B4P/BED2 | 1000021 | 100 | 0 | 0 | 0 | -
014/2B4P/LDK | 0100001F | 100 | 0 | 0 | 0 | -
015/2B4P/BED1 | 0100002D | 100 | 0 | 0 | 0 | -
015/2B4P/BED2 | 0100002E | 100 | 0 | 0 | 0 | -
015/2B4P/LDK | 1000031 | 100 | 0 | 0 | 0 | -
016/2B4P/BED1 | 1000034 | 100 | 0 | 0 | 0 | -
016/2B4P/BED2 | 1000035 | 100 | 0 | 0 | 0 | -
016/2B4P/LDK | 1000038 | 100 | 0 | 0 | 0 | -
017/2B4P/BED1 | 0100003B | 100 | 0 | 0 | 0 | -
017/2B4P/BED2 | 0100003C | 100 | 0 | 0 | 0 | -
017/2B4P/LDK | 0100003A | 100 | 0 | 0 | 0 | -
018/2B4P/BED1 | 1000044 | 100 | 0 | 0 | 0 | -
018/2B4P/BED2 | 1000045 | 100 | 0 | 0 | 0 | -
018/2B4P/LDK | 1000043 | 100 | 0 | 0 | 0 | -
Failed: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Unoccupied: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Note: | A TM 52 2013 analysis provides an assessment of comfort compliance based on bulk air modelling
i.e. each space is considered idealised and the air in the space perfectly mixed. The assessment does
not assess placement of space features e.g. windows & openings, airflow patterns or discomfort issues.
The user should assess these design aspects outside of the TM52 analysis.

## PASSIVE BRISE DSY2_TM52
Overall | [8 empty] | Operative temperature (TM 52/CIBSE) (°C) - hours in range |  |  | Operative temperature (TM 52/CIBSE) (°C) - hours in range
Passed: | 64 rooms: | [5 empty] | File | Location | > 26.10 | File | Location | > 26.10
Failed: | 0 rooms: | [5 empty] | PASSIVE BRISE DSY2.aps | 001/1B2P/BED | 17 | PASSIVE BRISE DSY2.aps | 001/1B2P/BED | 34 | 51
Unoccupied: | 0 rooms: | [5 empty] | PASSIVE BRISE DSY2.aps | 002/1B2P/BED | 17 | PASSIVE BRISE DSY2.aps | 002/1B2P/BED | 29 | 46
[7 empty] | PASSIVE BRISE DSY2.aps | 003/3B5P/BED1 | 17 | PASSIVE BRISE DSY2.aps | 003/3B5P/BED1 | 32 | 49
Data: | [6 empty] | PASSIVE BRISE DSY2.aps | 003/3B5P/BED2 | 18 | PASSIVE BRISE DSY2.aps | 003/3B5P/BED2 | 29 | 47
Building category: | Category II (new builds.) | [5 empty] | PASSIVE BRISE DSY2.aps | 003/3B5P/BED3 | 20 | PASSIVE BRISE DSY2.aps | 003/3B5P/BED3 | 31 | 51
Weather file: | London_LWC_DSY2_2020High50.epw | [5 empty] | PASSIVE BRISE DSY2.aps | 004/3B5P/BED1 | 18 | PASSIVE BRISE DSY2.aps | 004/3B5P/BED1 | 32 | 50
Days data= | 365 | 2021-01-01 | 2021-12-31 |  |  |  | PASSIVE BRISE DSY2.aps | 004/3B5P/BED2 | 20 | PASSIVE BRISE DSY2.aps | 004/3B5P/BED2 | 34 | 54
Days (summer)= | 153 | 2021-05-01 | 2021-09-30 |  |  |  | PASSIVE BRISE DSY2.aps | 004/3B5P/BED3 | 20 | PASSIVE BRISE DSY2.aps | 004/3B5P/BED3 | 31 | 51
Data OK? | OK | Full summer |  |  |  |  | PASSIVE BRISE DSY2.aps | 005/3B5P/BED1 | 18 | PASSIVE BRISE DSY2.aps | 005/3B5P/BED1 | 32 | 50
[7 empty] | PASSIVE BRISE DSY2.aps | 005/3B5P/BED2 | 20 | PASSIVE BRISE DSY2.aps | 005/3B5P/BED2 | 34 | 54
Occupancy: | [6 empty] | PASSIVE BRISE DSY2.aps | 005/3B5P/BED3 | 20 | PASSIVE BRISE DSY2.aps | 005/3B5P/BED3 | 31 | 51
Note: | This report assesses occupied periods only. Please be aware that TM52 should be conducted for occupied and/or “available hours”. | [5 empty] | PASSIVE BRISE DSY2.aps | 006/3B5P/BED1 | 17 | PASSIVE BRISE DSY2.aps | 006/3B5P/BED1 | 32 | 49
| Use of educational NCM profiles may be seen as inappropriate due to prolonged unoccupied periods during summer months. | [5 empty] | PASSIVE BRISE DSY2.aps | 006/3B5P/BED2 | 17 | PASSIVE BRISE DSY2.aps | 006/3B5P/BED2 | 29 | 46
| See Section 6.1.2 (a) of TM52 for further information. | [5 empty] | PASSIVE BRISE DSY2.aps | 006/3B5P/BED3 | 20 | PASSIVE BRISE DSY2.aps | 006/3B5P/BED3 | 31 | 51
[7 empty] | PASSIVE BRISE DSY2.aps | 007/1B2P/BED | 17 | PASSIVE BRISE DSY2.aps | 007/1B2P/BED | 29 | 46
Passed: | 64 rooms: | [5 empty] | PASSIVE BRISE DSY2.aps | 008/1B2P/BED | 18 | PASSIVE BRISE DSY2.aps | 008/1B2P/BED | 35 | 53
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing | PASSIVE BRISE DSY2.aps | 009/4B6P/BED1 | 20 | PASSIVE BRISE DSY2.aps | 009/4B6P/BED1 | 26 | 46
001/1B2P/BED | 2 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY2.aps | 009/4B6P/BED2 | 16 | PASSIVE BRISE DSY2.aps | 009/4B6P/BED2 | 14 | 30
001/1B2P/LDK | 0 | 100 | 0.1 | 2 | 1 | - | PASSIVE BRISE DSY2.aps | 009/4B6P/BED3 | 16 | PASSIVE BRISE DSY2.aps | 009/4B6P/BED3 | 19 | 35
002/1B2P/BED | 7 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY2.aps | 009/4B6P/BED4 | 20 | PASSIVE BRISE DSY2.aps | 009/4B6P/BED4 | 29 | 49
002/1B2P/LDK | 5 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY2.aps | 010/4B6P/BED1 | 20 | PASSIVE BRISE DSY2.aps | 010/4B6P/BED1 | 28 | 48
003/3B5P/BED1 | 0000005A | 100 | 0.2 | 6 | 1 | - | PASSIVE BRISE DSY2.aps | 010/4B6P/BED2 | 17 | PASSIVE BRISE DSY2.aps | 010/4B6P/BED2 | 14 | 31
003/3B5P/BED2 | 0000005B | 100 | 0.2 | 11 | 2 | 2 | PASSIVE BRISE DSY2.aps | 010/4B6P/BED3 | 17 | PASSIVE BRISE DSY2.aps | 010/4B6P/BED3 | 14 | 31
003/3B5P/BED3 | 0000005C | 100 | 0.8 | 16 | 2 | 2 | PASSIVE BRISE DSY2.aps | 010/4B6P/BED4 | 20 | PASSIVE BRISE DSY2.aps | 010/4B6P/BED4 | 31 | 51
003/3B5P/DINKIT | 0000000D | 100 | 0.3 | 4 | 1 | - | PASSIVE BRISE DSY2.aps | 011/2B4P/BED1 | 16 | PASSIVE BRISE DSY2.aps | 011/2B4P/BED1 | 21 | 37
003/3B5P/LIV | 0000000C | 100 | 0.4 | 7 | 1 | 2 | PASSIVE BRISE DSY2.aps | 011/2B4P/BED2 | 16 | PASSIVE BRISE DSY2.aps | 011/2B4P/BED2 | 21 | 37
004/3B5P/BED1 | 62 | 100 | 0.4 | 12 | 2 | 2 | PASSIVE BRISE DSY2.aps | 012/2B4P/BED1 | 16 | PASSIVE BRISE DSY2.aps | 012/2B4P/BED1 | 24 | 40
004/3B5P/BED2 | 63 | 100 | 0.6 | 14 | 2 | 2 | PASSIVE BRISE DSY2.aps | 012/2B4P/BED2 | 17 | PASSIVE BRISE DSY2.aps | 012/2B4P/BED2 | 22 | 39
004/3B5P/BED3 | 64 | 100 | 0.9 | 20 | 3 | 2 | PASSIVE BRISE DSY2.aps | 013/2B4P/BED1 | 16 | PASSIVE BRISE DSY2.aps | 013/2B4P/BED1 | 23 | 39
004/3B5P/DINKIT | 19 | 100 | 0.7 | 9 | 2 | 2 | PASSIVE BRISE DSY2.aps | 013/2B4P/BED2 | 17 | PASSIVE BRISE DSY2.aps | 013/2B4P/BED2 | 21 | 38
004/3B5P/LIV | 18 | 100 | 0.9 | 13 | 2 | 2 | PASSIVE BRISE DSY2.aps | 014/2B4P/BED1 | 17 | PASSIVE BRISE DSY2.aps | 014/2B4P/BED1 | 26 | 43
005/3B5P/BED1 | 69 | 100 | 0.4 | 12 | 2 | 2 | PASSIVE BRISE DSY2.aps | 014/2B4P/BED2 | 16 | PASSIVE BRISE DSY2.aps | 014/2B4P/BED2 | 24 | 40
005/3B5P/BED2 | 0000006A | 100 | 0.6 | 14 | 2 | 2 | PASSIVE BRISE DSY2.aps | 015/2B4P/BED1 | 17 | PASSIVE BRISE DSY2.aps | 015/2B4P/BED1 | 29 | 46
005/3B5P/BED3 | 0000006B | 100 | 0.9 | 20 | 3 | 2 | PASSIVE BRISE DSY2.aps | 015/2B4P/BED2 | 17 | PASSIVE BRISE DSY2.aps | 015/2B4P/BED2 | 28 | 45
005/3B5P/DINKIT | 0000001A | 100 | 0.7 | 9 | 2 | 2 | PASSIVE BRISE DSY2.aps | 016/2B4P/BED1 | 17 | PASSIVE BRISE DSY2.aps | 016/2B4P/BED1 | 29 | 46
005/3B5P/LIV | 0000001B | 100 | 0.9 | 13 | 2 | 2 | PASSIVE BRISE DSY2.aps | 016/2B4P/BED2 | 17 | PASSIVE BRISE DSY2.aps | 016/2B4P/BED2 | 28 | 45
006/3B5P/BED1 | 71 | 100 | 0.1 | 5 | 1 | - | PASSIVE BRISE DSY2.aps | 017/2B4P/BED1 | 17 | PASSIVE BRISE DSY2.aps | 017/2B4P/BED1 | 29 | 46
006/3B5P/BED2 | 70 | 100 | 0.2 | 9 | 2 | 2 | PASSIVE BRISE DSY2.aps | 017/2B4P/BED2 | 17 | PASSIVE BRISE DSY2.aps | 017/2B4P/BED2 | 28 | 45
006/3B5P/BED3 | 0000006F | 100 | 0.8 | 16 | 2 | 2 | PASSIVE BRISE DSY2.aps | 018/2B4P/BED1 | 17 | PASSIVE BRISE DSY2.aps | 018/2B4P/BED1 | 30 | 47
006/3B5P/DINKIT | 27 | 100 | 0.3 | 4 | 1 | - | PASSIVE BRISE DSY2.aps | 018/2B4P/BED2 | 17 | PASSIVE BRISE DSY2.aps | 018/2B4P/BED2 | 30 | 47
006/3B5P/LIV | 26 | 100 | 0.4 | 7 | 1 | 2 | PASSIVE BRISE DSY2.aps | Total hours | 707 | PASSIVE BRISE DSY2.aps | Total hours | 1093
007/1B2P/BED | 29 | 100 | 0 | 0 | 0 | -
007/1B2P/LDK | 28 | 100 | 0 | 0 | 0 | -
008/1B2P/BED | 31 | 100 | 0 | 0 | 0 | -
008/1B2P/LDK | 30 | 100 | 0.3 | 5 | 1 | -
009/4B6P/BED1 | 76 | 100 | 0.7 | 15 | 2 | 2
009/4B6P/BED2 | 77 | 100 | 0.2 | 6 | 1 | -
009/4B6P/BED3 | 78 | 100 | 0.2 | 12 | 2 | 2
009/4B6P/BED4 | 79 | 100 | 0.8 | 19 | 3 | 2
009/4B6P/DINKIT | 0000003D | 100 | 0.1 | 2 | 1 | -
009/4B6P/LIV | 0000003C | 100 | 0.4 | 7 | 1 | 2
010/4B6P/BED1 | 1000026 | 100 | 0.8 | 15 | 2 | 2
010/4B6P/BED2 | 1000027 | 100 | 0.2 | 6 | 1 | -
010/4B6P/BED3 | 1000028 | 100 | 0.2 | 12 | 2 | 2
010/4B6P/BED4 | 1000029 | 100 | 0.9 | 20 | 3 | 2
010/4B6P/DINKIT | 1000006 | 100 | 0.4 | 6 | 1 | -
010/4B6P/LIV | 1000005 | 100 | 0.7 | 13 | 2 | 2
011/2B4P/BED1 | 1000009 | 100 | 0 | 0 | 0 | -
011/2B4P/BED2 | 0100000A | 100 | 0 | 0 | 0 | -
011/2B4P/LDK | 1000008 | 100 | 0.1 | 2 | 1 | -
012/2B4P/BED1 | 1000011 | 100 | 0 | 0 | 0 | -
012/2B4P/BED2 | 1000012 | 100 | 0 | 0 | 0 | -
012/2B4P/LDK | 1000010 | 100 | 0.1 | 2 | 1 | -
013/2B4P/BED1 | 1000017 | 100 | 0 | 0 | 0 | -
013/2B4P/BED2 | 1000018 | 100 | 0 | 0 | 0 | -
013/2B4P/LDK | 1000016 | 100 | 0.1 | 2 | 1 | -
014/2B4P/BED1 | 1000020 | 100 | 0 | 0 | 0 | -
014/2B4P/BED2 | 1000021 | 100 | 0 | 0 | 0 | -
014/2B4P/LDK | 0100001F | 100 | 0.1 | 2 | 1 | -
015/2B4P/BED1 | 0100002D | 100 | 0 | 0 | 0 | -
015/2B4P/BED2 | 0100002E | 100 | 0.1 | 4 | 1 | -
015/2B4P/LDK | 1000031 | 100 | 0.2 | 4 | 1 | -
016/2B4P/BED1 | 1000034 | 100 | 0 | 0 | 0 | -
016/2B4P/BED2 | 1000035 | 100 | 0.1 | 2 | 1 | -
016/2B4P/LDK | 1000038 | 100 | 0.1 | 2 | 1 | -
017/2B4P/BED1 | 0100003B | 100 | 0 | 0 | 0 | -
017/2B4P/BED2 | 0100003C | 100 | 0.1 | 4 | 1 | -
017/2B4P/LDK | 0100003A | 100 | 0.3 | 4 | 1 | -
018/2B4P/BED1 | 1000044 | 100 | 0 | 0 | 0 | -
018/2B4P/BED2 | 1000045 | 100 | 0.1 | 5 | 1 | -
018/2B4P/LDK | 1000043 | 100 | 0.3 | 5 | 1 | -
Failed: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Unoccupied: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Note: | A TM 52 2013 analysis provides an assessment of comfort compliance based on bulk air modelling
i.e. each space is considered idealised and the air in the space perfectly mixed. The assessment does
not assess placement of space features e.g. windows & openings, airflow patterns or discomfort issues.
The user should assess these design aspects outside of the TM52 analysis.

## PASSIVE BRISE DSY3_TM52
Overall | [8 empty] | Operative temperature (TM 52/CIBSE) (°C) - hours in range |  |  | Operative temperature (TM 52/CIBSE) (°C) - hours in range
Passed: | 64 rooms: | [5 empty] | File | Location | > 26.10 | File | Location | > 26.10
Failed: | 0 rooms: | [5 empty] | PASSIVE BRISE DSY3.aps | 001/1B2P/BED | 21 | PASSIVE BRISE DSY3.aps | 001/1B2P/BED | 21 | 42
Unoccupied: | 0 rooms: | [5 empty] | PASSIVE BRISE DSY3.aps | 002/1B2P/BED | 21 | PASSIVE BRISE DSY3.aps | 002/1B2P/BED | 17 | 38
[7 empty] | PASSIVE BRISE DSY3.aps | 003/3B5P/BED1 | 21 | PASSIVE BRISE DSY3.aps | 003/3B5P/BED1 | 21 | 42
Data: | [6 empty] | PASSIVE BRISE DSY3.aps | 003/3B5P/BED2 | 21 | PASSIVE BRISE DSY3.aps | 003/3B5P/BED2 | 20 | 41
Building category: | Category II (new builds.) | [5 empty] | PASSIVE BRISE DSY3.aps | 003/3B5P/BED3 | 22 | PASSIVE BRISE DSY3.aps | 003/3B5P/BED3 | 21 | 43
Weather file: | London_LWC_DSY3_2020High50.epw | [5 empty] | PASSIVE BRISE DSY3.aps | 004/3B5P/BED1 | 22 | PASSIVE BRISE DSY3.aps | 004/3B5P/BED1 | 23 | 45
Days data= | 365 | 2021-01-01 | 2021-12-31 |  |  |  | PASSIVE BRISE DSY3.aps | 004/3B5P/BED2 | 23 | PASSIVE BRISE DSY3.aps | 004/3B5P/BED2 | 23 | 46
Days (summer)= | 153 | 2021-05-01 | 2021-09-30 |  |  |  | PASSIVE BRISE DSY3.aps | 004/3B5P/BED3 | 22 | PASSIVE BRISE DSY3.aps | 004/3B5P/BED3 | 24 | 46
Data OK? | OK | Full summer |  |  |  |  | PASSIVE BRISE DSY3.aps | 005/3B5P/BED1 | 22 | PASSIVE BRISE DSY3.aps | 005/3B5P/BED1 | 23 | 45
[7 empty] | PASSIVE BRISE DSY3.aps | 005/3B5P/BED2 | 23 | PASSIVE BRISE DSY3.aps | 005/3B5P/BED2 | 23 | 46
Occupancy: | [6 empty] | PASSIVE BRISE DSY3.aps | 005/3B5P/BED3 | 22 | PASSIVE BRISE DSY3.aps | 005/3B5P/BED3 | 24 | 46
Note: | This report assesses occupied periods only. Please be aware that TM52 should be conducted for occupied and/or “available hours”. | [5 empty] | PASSIVE BRISE DSY3.aps | 006/3B5P/BED1 | 21 | PASSIVE BRISE DSY3.aps | 006/3B5P/BED1 | 21 | 42
| Use of educational NCM profiles may be seen as inappropriate due to prolonged unoccupied periods during summer months. | [5 empty] | PASSIVE BRISE DSY3.aps | 006/3B5P/BED2 | 21 | PASSIVE BRISE DSY3.aps | 006/3B5P/BED2 | 20 | 41
| See Section 6.1.2 (a) of TM52 for further information. | [5 empty] | PASSIVE BRISE DSY3.aps | 006/3B5P/BED3 | 22 | PASSIVE BRISE DSY3.aps | 006/3B5P/BED3 | 21 | 43
[7 empty] | PASSIVE BRISE DSY3.aps | 007/1B2P/BED | 21 | PASSIVE BRISE DSY3.aps | 007/1B2P/BED | 17 | 38
Passed: | 64 rooms: | [5 empty] | PASSIVE BRISE DSY3.aps | 008/1B2P/BED | 21 | PASSIVE BRISE DSY3.aps | 008/1B2P/BED | 22 | 43
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing | PASSIVE BRISE DSY3.aps | 009/4B6P/BED1 | 22 | PASSIVE BRISE DSY3.aps | 009/4B6P/BED1 | 18 | 40
001/1B2P/BED | 2 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY3.aps | 009/4B6P/BED2 | 17 | PASSIVE BRISE DSY3.aps | 009/4B6P/BED2 | 10 | 27
001/1B2P/LDK | 0 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY3.aps | 009/4B6P/BED3 | 17 | PASSIVE BRISE DSY3.aps | 009/4B6P/BED3 | 14 | 31
002/1B2P/BED | 7 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY3.aps | 009/4B6P/BED4 | 22 | PASSIVE BRISE DSY3.aps | 009/4B6P/BED4 | 20 | 42
002/1B2P/LDK | 5 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY3.aps | 010/4B6P/BED1 | 22 | PASSIVE BRISE DSY3.aps | 010/4B6P/BED1 | 20 | 42
003/3B5P/BED1 | 0000005A | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY3.aps | 010/4B6P/BED2 | 17 | PASSIVE BRISE DSY3.aps | 010/4B6P/BED2 | 12 | 29
003/3B5P/BED2 | 0000005B | 100 | 0.3 | 6 | 1 | - | PASSIVE BRISE DSY3.aps | 010/4B6P/BED3 | 16 | PASSIVE BRISE DSY3.aps | 010/4B6P/BED3 | 9 | 25
003/3B5P/BED3 | 0000005C | 100 | 0.8 | 10 | 1 | 2 | PASSIVE BRISE DSY3.aps | 010/4B6P/BED4 | 22 | PASSIVE BRISE DSY3.aps | 010/4B6P/BED4 | 23 | 45
003/3B5P/DINKIT | 0000000D | 100 | 0.1 | 1 | 1 | - | PASSIVE BRISE DSY3.aps | 011/2B4P/BED1 | 18 | PASSIVE BRISE DSY3.aps | 011/2B4P/BED1 | 13 | 31
003/3B5P/LIV | 0000000C | 100 | 0.1 | 1 | 1 | - | PASSIVE BRISE DSY3.aps | 011/2B4P/BED2 | 18 | PASSIVE BRISE DSY3.aps | 011/2B4P/BED2 | 15 | 33
004/3B5P/BED1 | 62 | 100 | 0.5 | 7 | 1 | 2 | PASSIVE BRISE DSY3.aps | 012/2B4P/BED1 | 18 | PASSIVE BRISE DSY3.aps | 012/2B4P/BED1 | 15 | 33
004/3B5P/BED2 | 63 | 100 | 0.6 | 8 | 1 | 2 | PASSIVE BRISE DSY3.aps | 012/2B4P/BED2 | 19 | PASSIVE BRISE DSY3.aps | 012/2B4P/BED2 | 15 | 34
004/3B5P/BED3 | 64 | 100 | 0.9 | 13 | 2 | 2 | PASSIVE BRISE DSY3.aps | 013/2B4P/BED1 | 18 | PASSIVE BRISE DSY3.aps | 013/2B4P/BED1 | 15 | 33
004/3B5P/DINKIT | 19 | 100 | 0.3 | 2 | 1 | - | PASSIVE BRISE DSY3.aps | 013/2B4P/BED2 | 19 | PASSIVE BRISE DSY3.aps | 013/2B4P/BED2 | 16 | 35
004/3B5P/LIV | 18 | 100 | 0.8 | 6 | 1 | - | PASSIVE BRISE DSY3.aps | 014/2B4P/BED1 | 19 | PASSIVE BRISE DSY3.aps | 014/2B4P/BED1 | 16 | 35
005/3B5P/BED1 | 69 | 100 | 0.5 | 7 | 1 | 2 | PASSIVE BRISE DSY3.aps | 014/2B4P/BED2 | 18 | PASSIVE BRISE DSY3.aps | 014/2B4P/BED2 | 15 | 33
005/3B5P/BED2 | 0000006A | 100 | 0.6 | 8 | 1 | 2 | PASSIVE BRISE DSY3.aps | 015/2B4P/BED1 | 19 | PASSIVE BRISE DSY3.aps | 015/2B4P/BED1 | 17 | 36
005/3B5P/BED3 | 0000006B | 100 | 0.9 | 13 | 2 | 2 | PASSIVE BRISE DSY3.aps | 015/2B4P/BED2 | 20 | PASSIVE BRISE DSY3.aps | 015/2B4P/BED2 | 17 | 37
005/3B5P/DINKIT | 0000001A | 100 | 0.3 | 2 | 1 | - | PASSIVE BRISE DSY3.aps | 016/2B4P/BED1 | 19 | PASSIVE BRISE DSY3.aps | 016/2B4P/BED1 | 17 | 36
005/3B5P/LIV | 0000001B | 100 | 0.7 | 6 | 1 | - | PASSIVE BRISE DSY3.aps | 016/2B4P/BED2 | 20 | PASSIVE BRISE DSY3.aps | 016/2B4P/BED2 | 17 | 37
006/3B5P/BED1 | 71 | 100 | 0 | 0 | 0 | - | PASSIVE BRISE DSY3.aps | 017/2B4P/BED1 | 19 | PASSIVE BRISE DSY3.aps | 017/2B4P/BED1 | 17 | 36
006/3B5P/BED2 | 70 | 100 | 0.1 | 4 | 1 | - | PASSIVE BRISE DSY3.aps | 017/2B4P/BED2 | 20 | PASSIVE BRISE DSY3.aps | 017/2B4P/BED2 | 17 | 37
006/3B5P/BED3 | 0000006F | 100 | 0.8 | 10 | 1 | 2 | PASSIVE BRISE DSY3.aps | 018/2B4P/BED1 | 22 | PASSIVE BRISE DSY3.aps | 018/2B4P/BED1 | 17 | 39
006/3B5P/DINKIT | 27 | 100 | 0.1 | 1 | 1 | - | PASSIVE BRISE DSY3.aps | 018/2B4P/BED2 | 21 | PASSIVE BRISE DSY3.aps | 018/2B4P/BED2 | 17 | 38
006/3B5P/LIV | 26 | 100 | 0.1 | 1 | 1 | - | PASSIVE BRISE DSY3.aps | Total hours | 808 | PASSIVE BRISE DSY3.aps | Total hours | 723
007/1B2P/BED | 29 | 100 | 0 | 0 | 0 | -
007/1B2P/LDK | 28 | 100 | 0 | 0 | 0 | -
008/1B2P/BED | 31 | 100 | 0 | 0 | 0 | -
008/1B2P/LDK | 30 | 100 | 0 | 0 | 0 | -
009/4B6P/BED1 | 76 | 100 | 0.9 | 12 | 2 | 2
009/4B6P/BED2 | 77 | 100 | 0.1 | 3 | 1 | -
009/4B6P/BED3 | 78 | 100 | 0.2 | 4 | 1 | -
009/4B6P/BED4 | 79 | 100 | 0.9 | 12 | 2 | 2
009/4B6P/DINKIT | 0000003D | 100 | 0 | 0 | 0 | -
009/4B6P/LIV | 0000003C | 100 | 0.1 | 1 | 1 | -
010/4B6P/BED1 | 1000026 | 100 | 0.9 | 12 | 2 | 2
010/4B6P/BED2 | 1000027 | 100 | 0.2 | 5 | 1 | -
010/4B6P/BED3 | 1000028 | 100 | 0.2 | 4 | 1 | -
010/4B6P/BED4 | 1000029 | 100 | 0.9 | 12 | 2 | 2
010/4B6P/DINKIT | 1000006 | 100 | 0.3 | 2 | 1 | -
010/4B6P/LIV | 1000005 | 100 | 0.7 | 6 | 1 | -
011/2B4P/BED1 | 1000009 | 100 | 0 | 0 | 0 | -
011/2B4P/BED2 | 0100000A | 100 | 0 | 0 | 0 | -
011/2B4P/LDK | 1000008 | 100 | 0 | 0 | 0 | -
012/2B4P/BED1 | 1000011 | 100 | 0 | 0 | 0 | -
012/2B4P/BED2 | 1000012 | 100 | 0 | 0 | 0 | -
012/2B4P/LDK | 1000010 | 100 | 0 | 0 | 0 | -
013/2B4P/BED1 | 1000017 | 100 | 0 | 0 | 0 | -
013/2B4P/BED2 | 1000018 | 100 | 0 | 0 | 0 | -
013/2B4P/LDK | 1000016 | 100 | 0 | 0 | 0 | -
014/2B4P/BED1 | 1000020 | 100 | 0 | 0 | 0 | -
014/2B4P/BED2 | 1000021 | 100 | 0 | 0 | 0 | -
014/2B4P/LDK | 0100001F | 100 | 0 | 0 | 0 | -
015/2B4P/BED1 | 0100002D | 100 | 0 | 0 | 0 | -
015/2B4P/BED2 | 0100002E | 100 | 0 | 0 | 0 | -
015/2B4P/LDK | 1000031 | 100 | 0 | 0 | 0 | -
016/2B4P/BED1 | 1000034 | 100 | 0 | 0 | 0 | -
016/2B4P/BED2 | 1000035 | 100 | 0 | 0 | 0 | -
016/2B4P/LDK | 1000038 | 100 | 0.1 | 1 | 1 | -
017/2B4P/BED1 | 0100003B | 100 | 0 | 0 | 0 | -
017/2B4P/BED2 | 0100003C | 100 | 0 | 0 | 0 | -
017/2B4P/LDK | 0100003A | 100 | 0.2 | 1 | 1 | -
018/2B4P/BED1 | 1000044 | 100 | 0 | 0 | 0 | -
018/2B4P/BED2 | 1000045 | 100 | 0 | 0 | 0 | -
018/2B4P/LDK | 1000043 | 100 | 0.2 | 1 | 1 | -
Failed: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Unoccupied: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Note: | A TM 52 2013 analysis provides an assessment of comfort compliance based on bulk air modelling
i.e. each space is considered idealised and the air in the space perfectly mixed. The assessment does
not assess placement of space features e.g. windows & openings, airflow patterns or discomfort issues.
The user should assess these design aspects outside of the TM52 analysis.

## PASSIVE BLINDS DSY1_TM52
Overall | [8 empty] | Operative temperature (TM 52/CIBSE) (°C) - hours in range |  |  | Operative temperature (TM 52/CIBSE) (°C) - hours in range
Passed: | 64 rooms: | [5 empty] | File | Location | > 26.10 | File | Location | > 26.10
Failed: | 0 rooms: | [5 empty] | PASSIVE BLINDS DSY1.aps | 001/1B2P/BED | 7 | PASSIVE BLINDS DSY1.aps | 001/1B2P/BED | 6 | 13
Unoccupied: | 0 rooms: | [5 empty] | PASSIVE BLINDS DSY1.aps | 002/1B2P/BED | 7 | PASSIVE BLINDS DSY1.aps | 002/1B2P/BED | 5 | 12
[7 empty] | PASSIVE BLINDS DSY1.aps | 003/3B5P/BED1 | 8 | PASSIVE BLINDS DSY1.aps | 003/3B5P/BED1 | 7 | 15
Data: | [6 empty] | PASSIVE BLINDS DSY1.aps | 003/3B5P/BED2 | 9 | PASSIVE BLINDS DSY1.aps | 003/3B5P/BED2 | 6 | 15
Building category: | Category II (new builds.) | [5 empty] | PASSIVE BLINDS DSY1.aps | 003/3B5P/BED3 | 12 | PASSIVE BLINDS DSY1.aps | 003/3B5P/BED3 | 8 | 20
Weather file: | London_LWC_DSY1_2020High50.epw | [5 empty] | PASSIVE BLINDS DSY1.aps | 004/3B5P/BED1 | 9 | PASSIVE BLINDS DSY1.aps | 004/3B5P/BED1 | 8 | 17
Days data= | 365 | 2021-01-01 | 2021-12-31 |  |  |  | PASSIVE BLINDS DSY1.aps | 004/3B5P/BED2 | 10 | PASSIVE BLINDS DSY1.aps | 004/3B5P/BED2 | 8 | 18
Days (summer)= | 153 | 2021-05-01 | 2021-09-30 |  |  |  | PASSIVE BLINDS DSY1.aps | 004/3B5P/BED3 | 12 | PASSIVE BLINDS DSY1.aps | 004/3B5P/BED3 | 8 | 20
Data OK? | OK | Full summer |  |  |  |  | PASSIVE BLINDS DSY1.aps | 005/3B5P/BED1 | 9 | PASSIVE BLINDS DSY1.aps | 005/3B5P/BED1 | 8 | 17
[7 empty] | PASSIVE BLINDS DSY1.aps | 005/3B5P/BED2 | 10 | PASSIVE BLINDS DSY1.aps | 005/3B5P/BED2 | 8 | 18
Occupancy: | [6 empty] | PASSIVE BLINDS DSY1.aps | 005/3B5P/BED3 | 12 | PASSIVE BLINDS DSY1.aps | 005/3B5P/BED3 | 8 | 20
Note: | This report assesses occupied periods only. Please be aware that TM52 should be conducted for occupied and/or “available hours”. | [5 empty] | PASSIVE BLINDS DSY1.aps | 006/3B5P/BED1 | 8 | PASSIVE BLINDS DSY1.aps | 006/3B5P/BED1 | 7 | 15
| Use of educational NCM profiles may be seen as inappropriate due to prolonged unoccupied periods during summer months. | [5 empty] | PASSIVE BLINDS DSY1.aps | 006/3B5P/BED2 | 9 | PASSIVE BLINDS DSY1.aps | 006/3B5P/BED2 | 6 | 15
| See Section 6.1.2 (a) of TM52 for further information. | [5 empty] | PASSIVE BLINDS DSY1.aps | 006/3B5P/BED3 | 12 | PASSIVE BLINDS DSY1.aps | 006/3B5P/BED3 | 8 | 20
[7 empty] | PASSIVE BLINDS DSY1.aps | 007/1B2P/BED | 7 | PASSIVE BLINDS DSY1.aps | 007/1B2P/BED | 5 | 12
Passed: | 64 rooms: | [5 empty] | PASSIVE BLINDS DSY1.aps | 008/1B2P/BED | 9 | PASSIVE BLINDS DSY1.aps | 008/1B2P/BED | 8 | 17
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing | PASSIVE BLINDS DSY1.aps | 009/4B6P/BED1 | 12 | PASSIVE BLINDS DSY1.aps | 009/4B6P/BED1 | 7 | 19
001/1B2P/BED | 2 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 009/4B6P/BED2 | 7 | PASSIVE BLINDS DSY1.aps | 009/4B6P/BED2 | 2 | 9
001/1B2P/LDK | 0 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 009/4B6P/BED3 | 8 | PASSIVE BLINDS DSY1.aps | 009/4B6P/BED3 | 2 | 10
002/1B2P/BED | 7 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 009/4B6P/BED4 | 12 | PASSIVE BLINDS DSY1.aps | 009/4B6P/BED4 | 7 | 19
002/1B2P/LDK | 5 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 010/4B6P/BED1 | 12 | PASSIVE BLINDS DSY1.aps | 010/4B6P/BED1 | 7 | 19
003/3B5P/BED1 | 0000005A | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 010/4B6P/BED2 | 7 | PASSIVE BLINDS DSY1.aps | 010/4B6P/BED2 | 3 | 10
003/3B5P/BED2 | 0000005B | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 010/4B6P/BED3 | 7 | PASSIVE BLINDS DSY1.aps | 010/4B6P/BED3 | 3 | 10
003/3B5P/BED3 | 0000005C | 100 | 0.1 | 2 | 1 | - | PASSIVE BLINDS DSY1.aps | 010/4B6P/BED4 | 12 | PASSIVE BLINDS DSY1.aps | 010/4B6P/BED4 | 8 | 20
003/3B5P/DINKIT | 0000000D | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 011/2B4P/BED1 | 7 | PASSIVE BLINDS DSY1.aps | 011/2B4P/BED1 | 4 | 11
003/3B5P/LIV | 0000000C | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 011/2B4P/BED2 | 7 | PASSIVE BLINDS DSY1.aps | 011/2B4P/BED2 | 4 | 11
004/3B5P/BED1 | 62 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 012/2B4P/BED1 | 7 | PASSIVE BLINDS DSY1.aps | 012/2B4P/BED1 | 4 | 11
004/3B5P/BED2 | 63 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 012/2B4P/BED2 | 8 | PASSIVE BLINDS DSY1.aps | 012/2B4P/BED2 | 4 | 12
004/3B5P/BED3 | 64 | 100 | 0.2 | 6 | 1 | - | PASSIVE BLINDS DSY1.aps | 013/2B4P/BED1 | 7 | PASSIVE BLINDS DSY1.aps | 013/2B4P/BED1 | 4 | 11
004/3B5P/DINKIT | 19 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 013/2B4P/BED2 | 8 | PASSIVE BLINDS DSY1.aps | 013/2B4P/BED2 | 4 | 12
004/3B5P/LIV | 18 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 014/2B4P/BED1 | 7 | PASSIVE BLINDS DSY1.aps | 014/2B4P/BED1 | 5 | 12
005/3B5P/BED1 | 69 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 014/2B4P/BED2 | 7 | PASSIVE BLINDS DSY1.aps | 014/2B4P/BED2 | 4 | 11
005/3B5P/BED2 | 0000006A | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 015/2B4P/BED1 | 7 | PASSIVE BLINDS DSY1.aps | 015/2B4P/BED1 | 6 | 13
005/3B5P/BED3 | 0000006B | 100 | 0.2 | 6 | 1 | - | PASSIVE BLINDS DSY1.aps | 015/2B4P/BED2 | 8 | PASSIVE BLINDS DSY1.aps | 015/2B4P/BED2 | 6 | 14
005/3B5P/DINKIT | 0000001A | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 016/2B4P/BED1 | 7 | PASSIVE BLINDS DSY1.aps | 016/2B4P/BED1 | 5 | 12
005/3B5P/LIV | 0000001B | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 016/2B4P/BED2 | 8 | PASSIVE BLINDS DSY1.aps | 016/2B4P/BED2 | 5 | 13
006/3B5P/BED1 | 71 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 017/2B4P/BED1 | 8 | PASSIVE BLINDS DSY1.aps | 017/2B4P/BED1 | 5 | 13
006/3B5P/BED2 | 70 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 017/2B4P/BED2 | 8 | PASSIVE BLINDS DSY1.aps | 017/2B4P/BED2 | 6 | 14
006/3B5P/BED3 | 0000006F | 100 | 0.1 | 2 | 1 | - | PASSIVE BLINDS DSY1.aps | 018/2B4P/BED1 | 8 | PASSIVE BLINDS DSY1.aps | 018/2B4P/BED1 | 6 | 14
006/3B5P/DINKIT | 27 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | 018/2B4P/BED2 | 8 | PASSIVE BLINDS DSY1.aps | 018/2B4P/BED2 | 7 | 15
006/3B5P/LIV | 26 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY1.aps | Total hours | 347 | PASSIVE BLINDS DSY1.aps | Total hours | 232
007/1B2P/BED | 29 | 100 | 0 | 0 | 0 | -
007/1B2P/LDK | 28 | 100 | 0 | 0 | 0 | -
008/1B2P/BED | 31 | 100 | 0 | 0 | 0 | -
008/1B2P/LDK | 30 | 100 | 0 | 0 | 0 | -
009/4B6P/BED1 | 76 | 100 | 0.1 | 3 | 1 | -
009/4B6P/BED2 | 77 | 100 | 0 | 0 | 0 | -
009/4B6P/BED3 | 78 | 100 | 0 | 0 | 0 | -
009/4B6P/BED4 | 79 | 100 | 0.1 | 5 | 1 | -
009/4B6P/DINKIT | 0000003D | 100 | 0 | 0 | 0 | -
009/4B6P/LIV | 0000003C | 100 | 0 | 0 | 0 | -
010/4B6P/BED1 | 1000026 | 100 | 0.1 | 3 | 1 | -
010/4B6P/BED2 | 1000027 | 100 | 0 | 0 | 0 | -
010/4B6P/BED3 | 1000028 | 100 | 0 | 0 | 0 | -
010/4B6P/BED4 | 1000029 | 100 | 0.2 | 6 | 1 | -
010/4B6P/DINKIT | 1000006 | 100 | 0 | 0 | 0 | -
010/4B6P/LIV | 1000005 | 100 | 0 | 0 | 0 | -
011/2B4P/BED1 | 1000009 | 100 | 0 | 0 | 0 | -
011/2B4P/BED2 | 0100000A | 100 | 0 | 0 | 0 | -
011/2B4P/LDK | 1000008 | 100 | 0 | 0 | 0 | -
012/2B4P/BED1 | 1000011 | 100 | 0 | 0 | 0 | -
012/2B4P/BED2 | 1000012 | 100 | 0 | 0 | 0 | -
012/2B4P/LDK | 1000010 | 100 | 0 | 0 | 0 | -
013/2B4P/BED1 | 1000017 | 100 | 0 | 0 | 0 | -
013/2B4P/BED2 | 1000018 | 100 | 0 | 0 | 0 | -
013/2B4P/LDK | 1000016 | 100 | 0 | 0 | 0 | -
014/2B4P/BED1 | 1000020 | 100 | 0 | 0 | 0 | -
014/2B4P/BED2 | 1000021 | 100 | 0 | 0 | 0 | -
014/2B4P/LDK | 0100001F | 100 | 0 | 0 | 0 | -
015/2B4P/BED1 | 0100002D | 100 | 0 | 0 | 0 | -
015/2B4P/BED2 | 0100002E | 100 | 0 | 0 | 0 | -
015/2B4P/LDK | 1000031 | 100 | 0 | 0 | 0 | -
016/2B4P/BED1 | 1000034 | 100 | 0 | 0 | 0 | -
016/2B4P/BED2 | 1000035 | 100 | 0 | 0 | 0 | -
016/2B4P/LDK | 1000038 | 100 | 0 | 0 | 0 | -
017/2B4P/BED1 | 0100003B | 100 | 0 | 0 | 0 | -
017/2B4P/BED2 | 0100003C | 100 | 0 | 0 | 0 | -
017/2B4P/LDK | 0100003A | 100 | 0 | 0 | 0 | -
018/2B4P/BED1 | 1000044 | 100 | 0 | 0 | 0 | -
018/2B4P/BED2 | 1000045 | 100 | 0 | 0 | 0 | -
018/2B4P/LDK | 1000043 | 100 | 0 | 0 | 0 | -
Failed: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Unoccupied: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Note: | A TM 52 2013 analysis provides an assessment of comfort compliance based on bulk air modelling
i.e. each space is considered idealised and the air in the space perfectly mixed. The assessment does
not assess placement of space features e.g. windows & openings, airflow patterns or discomfort issues.
The user should assess these design aspects outside of the TM52 analysis.

## PASSIVE BLINDS DSY2_TM52
Overall | [8 empty] | Operative temperature (TM 52/CIBSE) (°C) - hours in range |  |  | Operative temperature (TM 52/CIBSE) (°C) - hours in range
Passed: | 64 rooms: | [5 empty] | File | Location | > 26.10 | File | Location | > 26.10
Failed: | 0 rooms: | [5 empty] | PASSIVE BLINDS DSY2.aps | 001/1B2P/BED | 18 | PASSIVE BLINDS DSY2.aps | 001/1B2P/BED | 36 | 54
Unoccupied: | 0 rooms: | [5 empty] | PASSIVE BLINDS DSY2.aps | 002/1B2P/BED | 17 | PASSIVE BLINDS DSY2.aps | 002/1B2P/BED | 31 | 48
[7 empty] | PASSIVE BLINDS DSY2.aps | 003/3B5P/BED1 | 17 | PASSIVE BLINDS DSY2.aps | 003/3B5P/BED1 | 35 | 52
Data: | [6 empty] | PASSIVE BLINDS DSY2.aps | 003/3B5P/BED2 | 19 | PASSIVE BLINDS DSY2.aps | 003/3B5P/BED2 | 32 | 51
Building category: | Category II (new builds.) | [5 empty] | PASSIVE BLINDS DSY2.aps | 003/3B5P/BED3 | 20 | PASSIVE BLINDS DSY2.aps | 003/3B5P/BED3 | 31 | 51
Weather file: | London_LWC_DSY2_2020High50.epw | [5 empty] | PASSIVE BLINDS DSY2.aps | 004/3B5P/BED1 | 19 | PASSIVE BLINDS DSY2.aps | 004/3B5P/BED1 | 34 | 53
Days data= | 365 | 2021-01-01 | 2021-12-31 |  |  |  | PASSIVE BLINDS DSY2.aps | 004/3B5P/BED2 | 21 | PASSIVE BLINDS DSY2.aps | 004/3B5P/BED2 | 36 | 57
Days (summer)= | 153 | 2021-05-01 | 2021-09-30 |  |  |  | PASSIVE BLINDS DSY2.aps | 004/3B5P/BED3 | 21 | PASSIVE BLINDS DSY2.aps | 004/3B5P/BED3 | 32 | 53
Data OK? | OK | Full summer |  |  |  |  | PASSIVE BLINDS DSY2.aps | 005/3B5P/BED1 | 19 | PASSIVE BLINDS DSY2.aps | 005/3B5P/BED1 | 34 | 53
[7 empty] | PASSIVE BLINDS DSY2.aps | 005/3B5P/BED2 | 21 | PASSIVE BLINDS DSY2.aps | 005/3B5P/BED2 | 36 | 57
Occupancy: | [6 empty] | PASSIVE BLINDS DSY2.aps | 005/3B5P/BED3 | 21 | PASSIVE BLINDS DSY2.aps | 005/3B5P/BED3 | 32 | 53
Note: | This report assesses occupied periods only. Please be aware that TM52 should be conducted for occupied and/or “available hours”. | [5 empty] | PASSIVE BLINDS DSY2.aps | 006/3B5P/BED1 | 17 | PASSIVE BLINDS DSY2.aps | 006/3B5P/BED1 | 35 | 52
| Use of educational NCM profiles may be seen as inappropriate due to prolonged unoccupied periods during summer months. | [5 empty] | PASSIVE BLINDS DSY2.aps | 006/3B5P/BED2 | 19 | PASSIVE BLINDS DSY2.aps | 006/3B5P/BED2 | 33 | 52
| See Section 6.1.2 (a) of TM52 for further information. | [5 empty] | PASSIVE BLINDS DSY2.aps | 006/3B5P/BED3 | 20 | PASSIVE BLINDS DSY2.aps | 006/3B5P/BED3 | 31 | 51
[7 empty] | PASSIVE BLINDS DSY2.aps | 007/1B2P/BED | 17 | PASSIVE BLINDS DSY2.aps | 007/1B2P/BED | 31 | 48
Passed: | 64 rooms: | [5 empty] | PASSIVE BLINDS DSY2.aps | 008/1B2P/BED | 18 | PASSIVE BLINDS DSY2.aps | 008/1B2P/BED | 39 | 57
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing | PASSIVE BLINDS DSY2.aps | 009/4B6P/BED1 | 20 | PASSIVE BLINDS DSY2.aps | 009/4B6P/BED1 | 29 | 49
001/1B2P/BED | 2 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY2.aps | 009/4B6P/BED2 | 16 | PASSIVE BLINDS DSY2.aps | 009/4B6P/BED2 | 15 | 31
001/1B2P/LDK | 0 | 100 | 0.4 | 7 | 1 | 2 | PASSIVE BLINDS DSY2.aps | 009/4B6P/BED3 | 16 | PASSIVE BLINDS DSY2.aps | 009/4B6P/BED3 | 19 | 35
002/1B2P/BED | 7 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY2.aps | 009/4B6P/BED4 | 20 | PASSIVE BLINDS DSY2.aps | 009/4B6P/BED4 | 32 | 52
002/1B2P/LDK | 5 | 100 | 0.1 | 1 | 1 | - | PASSIVE BLINDS DSY2.aps | 010/4B6P/BED1 | 20 | PASSIVE BLINDS DSY2.aps | 010/4B6P/BED1 | 32 | 52
003/3B5P/BED1 | 0000005A | 100 | 0.2 | 7 | 1 | 2 | PASSIVE BLINDS DSY2.aps | 010/4B6P/BED2 | 17 | PASSIVE BLINDS DSY2.aps | 010/4B6P/BED2 | 16 | 33
003/3B5P/BED2 | 0000005B | 100 | 0.7 | 16 | 2 | 2 | PASSIVE BLINDS DSY2.aps | 010/4B6P/BED3 | 17 | PASSIVE BLINDS DSY2.aps | 010/4B6P/BED3 | 14 | 31
003/3B5P/BED3 | 0000005C | 100 | 1.1 | 24 | 3 | 2 | PASSIVE BLINDS DSY2.aps | 010/4B6P/BED4 | 20 | PASSIVE BLINDS DSY2.aps | 010/4B6P/BED4 | 32 | 52
003/3B5P/DINKIT | 0000000D | 100 | 0.7 | 10 | 2 | 2 | PASSIVE BLINDS DSY2.aps | 011/2B4P/BED1 | 16 | PASSIVE BLINDS DSY2.aps | 011/2B4P/BED1 | 25 | 41
003/3B5P/LIV | 0000000C | 100 | 0.8 | 12 | 2 | 2 | PASSIVE BLINDS DSY2.aps | 011/2B4P/BED2 | 17 | PASSIVE BLINDS DSY2.aps | 011/2B4P/BED2 | 25 | 42
004/3B5P/BED1 | 62 | 100 | 0.6 | 14 | 2 | 2 | PASSIVE BLINDS DSY2.aps | 012/2B4P/BED1 | 16 | PASSIVE BLINDS DSY2.aps | 012/2B4P/BED1 | 25 | 41
004/3B5P/BED2 | 63 | 100 | 1 | 21 | 3 | 2 | PASSIVE BLINDS DSY2.aps | 012/2B4P/BED2 | 17 | PASSIVE BLINDS DSY2.aps | 012/2B4P/BED2 | 22 | 39
004/3B5P/BED3 | 64 | 100 | 1.1 | 26 | 4 | 2 | PASSIVE BLINDS DSY2.aps | 013/2B4P/BED1 | 17 | PASSIVE BLINDS DSY2.aps | 013/2B4P/BED1 | 24 | 41
004/3B5P/DINKIT | 19 | 100 | 1.2 | 14 | 2 | 2 | PASSIVE BLINDS DSY2.aps | 013/2B4P/BED2 | 17 | PASSIVE BLINDS DSY2.aps | 013/2B4P/BED2 | 22 | 39
004/3B5P/LIV | 18 | 100 | 1.6 | 18 | 3 | 2 | PASSIVE BLINDS DSY2.aps | 014/2B4P/BED1 | 17 | PASSIVE BLINDS DSY2.aps | 014/2B4P/BED1 | 29 | 46
005/3B5P/BED1 | 69 | 100 | 0.6 | 14 | 2 | 2 | PASSIVE BLINDS DSY2.aps | 014/2B4P/BED2 | 17 | PASSIVE BLINDS DSY2.aps | 014/2B4P/BED2 | 28 | 45
005/3B5P/BED2 | 0000006A | 100 | 1 | 21 | 3 | 2 | PASSIVE BLINDS DSY2.aps | 015/2B4P/BED1 | 17 | PASSIVE BLINDS DSY2.aps | 015/2B4P/BED1 | 32 | 49
005/3B5P/BED3 | 0000006B | 100 | 1.1 | 26 | 4 | 2 | PASSIVE BLINDS DSY2.aps | 015/2B4P/BED2 | 17 | PASSIVE BLINDS DSY2.aps | 015/2B4P/BED2 | 32 | 49
005/3B5P/DINKIT | 0000001A | 100 | 1.2 | 14 | 2 | 2 | PASSIVE BLINDS DSY2.aps | 016/2B4P/BED1 | 17 | PASSIVE BLINDS DSY2.aps | 016/2B4P/BED1 | 30 | 47
005/3B5P/LIV | 0000001B | 100 | 1.6 | 18 | 3 | 2 | PASSIVE BLINDS DSY2.aps | 016/2B4P/BED2 | 17 | PASSIVE BLINDS DSY2.aps | 016/2B4P/BED2 | 30 | 47
006/3B5P/BED1 | 71 | 100 | 0.2 | 6 | 1 | - | PASSIVE BLINDS DSY2.aps | 017/2B4P/BED1 | 17 | PASSIVE BLINDS DSY2.aps | 017/2B4P/BED1 | 31 | 48
006/3B5P/BED2 | 70 | 100 | 0.6 | 14 | 2 | 2 | PASSIVE BLINDS DSY2.aps | 017/2B4P/BED2 | 17 | PASSIVE BLINDS DSY2.aps | 017/2B4P/BED2 | 31 | 48
006/3B5P/BED3 | 0000006F | 100 | 1 | 22 | 3 | 2 | PASSIVE BLINDS DSY2.aps | 018/2B4P/BED1 | 18 | PASSIVE BLINDS DSY2.aps | 018/2B4P/BED1 | 33 | 51
006/3B5P/DINKIT | 27 | 100 | 0.6 | 10 | 2 | 2 | PASSIVE BLINDS DSY2.aps | 018/2B4P/BED2 | 18 | PASSIVE BLINDS DSY2.aps | 018/2B4P/BED2 | 33 | 51
006/3B5P/LIV | 26 | 100 | 0.8 | 12 | 2 | 2 | PASSIVE BLINDS DSY2.aps | Total hours | 722 | PASSIVE BLINDS DSY2.aps | Total hours | 1179
007/1B2P/BED | 29 | 100 | 0 | 0 | 0 | -
007/1B2P/LDK | 28 | 100 | 0.1 | 1 | 1 | -
008/1B2P/BED | 31 | 100 | 0.1 | 2 | 1 | -
008/1B2P/LDK | 30 | 100 | 0.6 | 11 | 2 | 2
009/4B6P/BED1 | 76 | 100 | 0.9 | 20 | 3 | 2
009/4B6P/BED2 | 77 | 100 | 0.3 | 10 | 2 | 2
009/4B6P/BED3 | 78 | 100 | 0.6 | 14 | 2 | 2
009/4B6P/BED4 | 79 | 100 | 1 | 23 | 4 | 2
009/4B6P/DINKIT | 0000003D | 100 | 0.4 | 6 | 1 | -
009/4B6P/LIV | 0000003C | 100 | 1.4 | 17 | 3 | 2
010/4B6P/BED1 | 1000026 | 100 | 0.9 | 20 | 3 | 2
010/4B6P/BED2 | 1000027 | 100 | 0.3 | 13 | 2 | 2
010/4B6P/BED3 | 1000028 | 100 | 0.6 | 15 | 2 | 2
010/4B6P/BED4 | 1000029 | 100 | 1 | 25 | 4 | 2
010/4B6P/DINKIT | 1000006 | 100 | 0.7 | 15 | 2 | 2
010/4B6P/LIV | 1000005 | 100 | 1.6 | 21 | 3 | 2
011/2B4P/BED1 | 1000009 | 100 | 0 | 0 | 0 | -
011/2B4P/BED2 | 0100000A | 100 | 0 | 0 | 0 | -
011/2B4P/LDK | 1000008 | 100 | 0.2 | 4 | 1 | -
012/2B4P/BED1 | 1000011 | 100 | 0 | 0 | 0 | -
012/2B4P/BED2 | 1000012 | 100 | 0.1 | 2 | 1 | -
012/2B4P/LDK | 1000010 | 100 | 0.1 | 2 | 1 | -
013/2B4P/BED1 | 1000017 | 100 | 0 | 0 | 0 | -
013/2B4P/BED2 | 1000018 | 100 | 0.1 | 2 | 1 | -
013/2B4P/LDK | 1000016 | 100 | 0.1 | 2 | 1 | -
014/2B4P/BED1 | 1000020 | 100 | 0 | 0 | 0 | -
014/2B4P/BED2 | 1000021 | 100 | 0.1 | 2 | 1 | -
014/2B4P/LDK | 0100001F | 100 | 0.1 | 2 | 1 | -
015/2B4P/BED1 | 0100002D | 100 | 0 | 0 | 0 | -
015/2B4P/BED2 | 0100002E | 100 | 0.2 | 8 | 1 | 2
015/2B4P/LDK | 1000031 | 100 | 0.7 | 14 | 2 | 2
016/2B4P/BED1 | 1000034 | 100 | 0 | 0 | 0 | -
016/2B4P/BED2 | 1000035 | 100 | 0.1 | 5 | 1 | -
016/2B4P/LDK | 1000038 | 100 | 0.6 | 12 | 2 | 2
017/2B4P/BED1 | 0100003B | 100 | 0 | 1 | 1 | -
017/2B4P/BED2 | 0100003C | 100 | 0.2 | 6 | 1 | -
017/2B4P/LDK | 0100003A | 100 | 0.7 | 12 | 2 | 2
018/2B4P/BED1 | 1000044 | 100 | 0.1 | 4 | 1 | -
018/2B4P/BED2 | 1000045 | 100 | 0.2 | 9 | 2 | 2
018/2B4P/LDK | 1000043 | 100 | 0.9 | 14 | 2 | 2
Failed: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Unoccupied: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Note: | A TM 52 2013 analysis provides an assessment of comfort compliance based on bulk air modelling
i.e. each space is considered idealised and the air in the space perfectly mixed. The assessment does
not assess placement of space features e.g. windows & openings, airflow patterns or discomfort issues.
The user should assess these design aspects outside of the TM52 analysis.

## PASSIVE BLINDS DSY3_TM52
Overall | [8 empty] | Operative temperature (TM 52/CIBSE) (°C) - hours in range |  |  | Operative temperature (TM 52/CIBSE) (°C) - hours in range
Passed: | 64 rooms: | [5 empty] | File | Location | > 26.10 | File | Location | > 26.10
Failed: | 0 rooms: | [5 empty] | PASSIVE BLINDS DSY3.aps | 001/1B2P/BED | 21 | PASSIVE BLINDS DSY3.aps | 001/1B2P/BED | 22 | 43
Unoccupied: | 0 rooms: | [5 empty] | PASSIVE BLINDS DSY3.aps | 002/1B2P/BED | 21 | PASSIVE BLINDS DSY3.aps | 002/1B2P/BED | 18 | 39
[7 empty] | PASSIVE BLINDS DSY3.aps | 003/3B5P/BED1 | 22 | PASSIVE BLINDS DSY3.aps | 003/3B5P/BED1 | 22 | 44
Data: | [6 empty] | PASSIVE BLINDS DSY3.aps | 003/3B5P/BED2 | 21 | PASSIVE BLINDS DSY3.aps | 003/3B5P/BED2 | 22 | 43
Building category: | Category II (new builds.) | [5 empty] | PASSIVE BLINDS DSY3.aps | 003/3B5P/BED3 | 22 | PASSIVE BLINDS DSY3.aps | 003/3B5P/BED3 | 24 | 46
Weather file: | London_LWC_DSY3_2020High50.epw | [5 empty] | PASSIVE BLINDS DSY3.aps | 004/3B5P/BED1 | 22 | PASSIVE BLINDS DSY3.aps | 004/3B5P/BED1 | 23 | 45
Days data= | 365 | 2021-01-01 | 2021-12-31 |  |  |  | PASSIVE BLINDS DSY3.aps | 004/3B5P/BED2 | 26 | PASSIVE BLINDS DSY3.aps | 004/3B5P/BED2 | 25 | 51
Days (summer)= | 153 | 2021-05-01 | 2021-09-30 |  |  |  | PASSIVE BLINDS DSY3.aps | 004/3B5P/BED3 | 22 | PASSIVE BLINDS DSY3.aps | 004/3B5P/BED3 | 24 | 46
Data OK? | OK | Full summer |  |  |  |  | PASSIVE BLINDS DSY3.aps | 005/3B5P/BED1 | 22 | PASSIVE BLINDS DSY3.aps | 005/3B5P/BED1 | 23 | 45
[7 empty] | PASSIVE BLINDS DSY3.aps | 005/3B5P/BED2 | 26 | PASSIVE BLINDS DSY3.aps | 005/3B5P/BED2 | 25 | 51
Occupancy: | [6 empty] | PASSIVE BLINDS DSY3.aps | 005/3B5P/BED3 | 22 | PASSIVE BLINDS DSY3.aps | 005/3B5P/BED3 | 24 | 46
Note: | This report assesses occupied periods only. Please be aware that TM52 should be conducted for occupied and/or “available hours”. | [5 empty] | PASSIVE BLINDS DSY3.aps | 006/3B5P/BED1 | 22 | PASSIVE BLINDS DSY3.aps | 006/3B5P/BED1 | 22 | 44
| Use of educational NCM profiles may be seen as inappropriate due to prolonged unoccupied periods during summer months. | [5 empty] | PASSIVE BLINDS DSY3.aps | 006/3B5P/BED2 | 22 | PASSIVE BLINDS DSY3.aps | 006/3B5P/BED2 | 21 | 43
| See Section 6.1.2 (a) of TM52 for further information. | [5 empty] | PASSIVE BLINDS DSY3.aps | 006/3B5P/BED3 | 22 | PASSIVE BLINDS DSY3.aps | 006/3B5P/BED3 | 24 | 46
[7 empty] | PASSIVE BLINDS DSY3.aps | 007/1B2P/BED | 21 | PASSIVE BLINDS DSY3.aps | 007/1B2P/BED | 18 | 39
Passed: | 64 rooms: | [5 empty] | PASSIVE BLINDS DSY3.aps | 008/1B2P/BED | 23 | PASSIVE BLINDS DSY3.aps | 008/1B2P/BED | 24 | 47
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing | PASSIVE BLINDS DSY3.aps | 009/4B6P/BED1 | 22 | PASSIVE BLINDS DSY3.aps | 009/4B6P/BED1 | 20 | 42
001/1B2P/BED | 2 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY3.aps | 009/4B6P/BED2 | 18 | PASSIVE BLINDS DSY3.aps | 009/4B6P/BED2 | 11 | 29
001/1B2P/LDK | 0 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY3.aps | 009/4B6P/BED3 | 19 | PASSIVE BLINDS DSY3.aps | 009/4B6P/BED3 | 15 | 34
002/1B2P/BED | 7 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY3.aps | 009/4B6P/BED4 | 23 | PASSIVE BLINDS DSY3.aps | 009/4B6P/BED4 | 23 | 46
002/1B2P/LDK | 5 | 100 | 0 | 0 | 0 | - | PASSIVE BLINDS DSY3.aps | 010/4B6P/BED1 | 22 | PASSIVE BLINDS DSY3.aps | 010/4B6P/BED1 | 22 | 44
003/3B5P/BED1 | 0000005A | 100 | 0.1 | 5 | 1 | - | PASSIVE BLINDS DSY3.aps | 010/4B6P/BED2 | 18 | PASSIVE BLINDS DSY3.aps | 010/4B6P/BED2 | 13 | 31
003/3B5P/BED2 | 0000005B | 100 | 0.7 | 9 | 1 | 2 | PASSIVE BLINDS DSY3.aps | 010/4B6P/BED3 | 17 | PASSIVE BLINDS DSY3.aps | 010/4B6P/BED3 | 10 | 27
003/3B5P/BED3 | 0000005C | 100 | 1 | 18 | 2 | 2 | PASSIVE BLINDS DSY3.aps | 010/4B6P/BED4 | 24 | PASSIVE BLINDS DSY3.aps | 010/4B6P/BED4 | 24 | 48
003/3B5P/DINKIT | 0000000D | 100 | 0.3 | 2 | 1 | - | PASSIVE BLINDS DSY3.aps | 011/2B4P/BED1 | 18 | PASSIVE BLINDS DSY3.aps | 011/2B4P/BED1 | 15 | 33
003/3B5P/LIV | 0000000C | 100 | 0.6 | 6 | 1 | - | PASSIVE BLINDS DSY3.aps | 011/2B4P/BED2 | 19 | PASSIVE BLINDS DSY3.aps | 011/2B4P/BED2 | 16 | 35
004/3B5P/BED1 | 62 | 100 | 0.7 | 9 | 1 | 2 | PASSIVE BLINDS DSY3.aps | 012/2B4P/BED1 | 18 | PASSIVE BLINDS DSY3.aps | 012/2B4P/BED1 | 16 | 34
004/3B5P/BED2 | 63 | 100 | 1 | 14 | 2 | 2 | PASSIVE BLINDS DSY3.aps | 012/2B4P/BED2 | 19 | PASSIVE BLINDS DSY3.aps | 012/2B4P/BED2 | 16 | 35
004/3B5P/BED3 | 64 | 100 | 1.2 | 20 | 2 | 2 | PASSIVE BLINDS DSY3.aps | 013/2B4P/BED1 | 18 | PASSIVE BLINDS DSY3.aps | 013/2B4P/BED1 | 16 | 34
004/3B5P/DINKIT | 19 | 100 | 0.7 | 6 | 1 | - | PASSIVE BLINDS DSY3.aps | 013/2B4P/BED2 | 20 | PASSIVE BLINDS DSY3.aps | 013/2B4P/BED2 | 16 | 36
004/3B5P/LIV | 18 | 100 | 1.3 | 10 | 2 | 2 | PASSIVE BLINDS DSY3.aps | 014/2B4P/BED1 | 20 | PASSIVE BLINDS DSY3.aps | 014/2B4P/BED1 | 17 | 37
005/3B5P/BED1 | 69 | 100 | 0.7 | 9 | 1 | 2 | PASSIVE BLINDS DSY3.aps | 014/2B4P/BED2 | 20 | PASSIVE BLINDS DSY3.aps | 014/2B4P/BED2 | 16 | 36
005/3B5P/BED2 | 0000006A | 100 | 1 | 14 | 2 | 2 | PASSIVE BLINDS DSY3.aps | 015/2B4P/BED1 | 22 | PASSIVE BLINDS DSY3.aps | 015/2B4P/BED1 | 18 | 40
005/3B5P/BED3 | 0000006B | 100 | 1.2 | 20 | 2 | 2 | PASSIVE BLINDS DSY3.aps | 015/2B4P/BED2 | 22 | PASSIVE BLINDS DSY3.aps | 015/2B4P/BED2 | 19 | 41
005/3B5P/DINKIT | 0000001A | 100 | 0.7 | 6 | 1 | - | PASSIVE BLINDS DSY3.aps | 016/2B4P/BED1 | 21 | PASSIVE BLINDS DSY3.aps | 016/2B4P/BED1 | 18 | 39
005/3B5P/LIV | 0000001B | 100 | 1.3 | 10 | 2 | 2 | PASSIVE BLINDS DSY3.aps | 016/2B4P/BED2 | 20 | PASSIVE BLINDS DSY3.aps | 016/2B4P/BED2 | 19 | 39
006/3B5P/BED1 | 71 | 100 | 0.1 | 5 | 1 | - | PASSIVE BLINDS DSY3.aps | 017/2B4P/BED1 | 22 | PASSIVE BLINDS DSY3.aps | 017/2B4P/BED1 | 18 | 40
006/3B5P/BED2 | 70 | 100 | 0.6 | 8 | 1 | 2 | PASSIVE BLINDS DSY3.aps | 017/2B4P/BED2 | 21 | PASSIVE BLINDS DSY3.aps | 017/2B4P/BED2 | 19 | 40
006/3B5P/BED3 | 0000006F | 100 | 1 | 18 | 2 | 2 | PASSIVE BLINDS DSY3.aps | 018/2B4P/BED1 | 22 | PASSIVE BLINDS DSY3.aps | 018/2B4P/BED1 | 20 | 42
006/3B5P/DINKIT | 27 | 100 | 0.2 | 2 | 1 | - | PASSIVE BLINDS DSY3.aps | 018/2B4P/BED2 | 22 | PASSIVE BLINDS DSY3.aps | 018/2B4P/BED2 | 21 | 43
006/3B5P/LIV | 26 | 100 | 0.6 | 6 | 1 | - | PASSIVE BLINDS DSY3.aps | Total hours | 844 | PASSIVE BLINDS DSY3.aps | Total hours | 779
007/1B2P/BED | 29 | 100 | 0 | 0 | 0 | -
007/1B2P/LDK | 28 | 100 | 0 | 0 | 0 | -
008/1B2P/BED | 31 | 100 | 0 | 0 | 0 | -
008/1B2P/LDK | 30 | 100 | 0.2 | 2 | 1 | -
009/4B6P/BED1 | 76 | 100 | 1 | 18 | 2 | 2
009/4B6P/BED2 | 77 | 100 | 0.4 | 6 | 1 | -
009/4B6P/BED3 | 78 | 100 | 0.7 | 9 | 1 | 2
009/4B6P/BED4 | 79 | 100 | 1.1 | 19 | 2 | 2
009/4B6P/DINKIT | 0000003D | 100 | 0.3 | 2 | 1 | -
009/4B6P/LIV | 0000003C | 100 | 1.2 | 8 | 1 | 2
010/4B6P/BED1 | 1000026 | 100 | 1 | 18 | 2 | 2
010/4B6P/BED2 | 1000027 | 100 | 0.5 | 8 | 1 | 2
010/4B6P/BED3 | 1000028 | 100 | 0.8 | 9 | 1 | 2
010/4B6P/BED4 | 1000029 | 100 | 1.2 | 19 | 2 | 2
010/4B6P/DINKIT | 1000006 | 100 | 1 | 7 | 1 | 2
010/4B6P/LIV | 1000005 | 100 | 1.6 | 14 | 2 | 2
011/2B4P/BED1 | 1000009 | 100 | 0 | 0 | 0 | -
011/2B4P/BED2 | 0100000A | 100 | 0 | 0 | 0 | -
011/2B4P/LDK | 1000008 | 100 | 0 | 0 | 0 | -
012/2B4P/BED1 | 1000011 | 100 | 0 | 0 | 0 | -
012/2B4P/BED2 | 1000012 | 100 | 0 | 0 | 0 | -
012/2B4P/LDK | 1000010 | 100 | 0 | 0 | 0 | -
013/2B4P/BED1 | 1000017 | 100 | 0 | 0 | 0 | -
013/2B4P/BED2 | 1000018 | 100 | 0 | 0 | 0 | -
013/2B4P/LDK | 1000016 | 100 | 0 | 0 | 0 | -
014/2B4P/BED1 | 1000020 | 100 | 0 | 0 | 0 | -
014/2B4P/BED2 | 1000021 | 100 | 0 | 0 | 0 | -
014/2B4P/LDK | 0100001F | 100 | 0 | 0 | 0 | -
015/2B4P/BED1 | 0100002D | 100 | 0 | 0 | 0 | -
015/2B4P/BED2 | 0100002E | 100 | 0 | 0 | 0 | -
015/2B4P/LDK | 1000031 | 100 | 0.3 | 2 | 1 | -
016/2B4P/BED1 | 1000034 | 100 | 0 | 0 | 0 | -
016/2B4P/BED2 | 1000035 | 100 | 0 | 0 | 0 | -
016/2B4P/LDK | 1000038 | 100 | 0.3 | 2 | 1 | -
017/2B4P/BED1 | 0100003B | 100 | 0 | 0 | 0 | -
017/2B4P/BED2 | 0100003C | 100 | 0 | 0 | 0 | -
017/2B4P/LDK | 0100003A | 100 | 0.6 | 4 | 1 | -
018/2B4P/BED1 | 1000044 | 100 | 0 | 0 | 0 | -
018/2B4P/BED2 | 1000045 | 100 | 0 | 0 | 0 | -
018/2B4P/LDK | 1000043 | 100 | 0.7 | 5 | 1 | -
Failed: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Unoccupied: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Note: | A TM 52 2013 analysis provides an assessment of comfort compliance based on bulk air modelling
i.e. each space is considered idealised and the air in the space perfectly mixed. The assessment does
not assess placement of space features e.g. windows & openings, airflow patterns or discomfort issues.
The user should assess these design aspects outside of the TM52 analysis.

## PASSIVE 1.5ACH DSY1_TM52
Overall | [8 empty] | Operative temperature (TM 52/CIBSE) (°C) - hours in range |  |  | Operative temperature (TM 52/CIBSE) (°C) - hours in range
Passed: | 64 rooms: | [5 empty] | File | Location | > 26.10 | File | Location | > 26.10
Failed: | 0 rooms: | [5 empty] | PASSIVE 1.5ACH DSY1.aps | 001/1B2P/BED | 7 | PASSIVE 1.5ACH DSY1.aps | 001/1B2P/BED | 6 | 13
Unoccupied: | 0 rooms: | [5 empty] | PASSIVE 1.5ACH DSY1.aps | 002/1B2P/BED | 7 | PASSIVE 1.5ACH DSY1.aps | 002/1B2P/BED | 4 | 11
[7 empty] | PASSIVE 1.5ACH DSY1.aps | 003/3B5P/BED1 | 8 | PASSIVE 1.5ACH DSY1.aps | 003/3B5P/BED1 | 6 | 14
Data: | [6 empty] | PASSIVE 1.5ACH DSY1.aps | 003/3B5P/BED2 | 9 | PASSIVE 1.5ACH DSY1.aps | 003/3B5P/BED2 | 6 | 15
Building category: | Category II (new builds.) | [5 empty] | PASSIVE 1.5ACH DSY1.aps | 003/3B5P/BED3 | 12 | PASSIVE 1.5ACH DSY1.aps | 003/3B5P/BED3 | 7 | 19
Weather file: | London_LWC_DSY1_2020High50.epw | [5 empty] | PASSIVE 1.5ACH DSY1.aps | 004/3B5P/BED1 | 9 | PASSIVE 1.5ACH DSY1.aps | 004/3B5P/BED1 | 7 | 16
Days data= | 365 | 2021-01-01 | 2021-12-31 |  |  |  | PASSIVE 1.5ACH DSY1.aps | 004/3B5P/BED2 | 11 | PASSIVE 1.5ACH DSY1.aps | 004/3B5P/BED2 | 7 | 18
Days (summer)= | 153 | 2021-05-01 | 2021-09-30 |  |  |  | PASSIVE 1.5ACH DSY1.aps | 004/3B5P/BED3 | 12 | PASSIVE 1.5ACH DSY1.aps | 004/3B5P/BED3 | 7 | 19
Data OK? | OK | Full summer |  |  |  |  | PASSIVE 1.5ACH DSY1.aps | 005/3B5P/BED1 | 9 | PASSIVE 1.5ACH DSY1.aps | 005/3B5P/BED1 | 7 | 16
[7 empty] | PASSIVE 1.5ACH DSY1.aps | 005/3B5P/BED2 | 11 | PASSIVE 1.5ACH DSY1.aps | 005/3B5P/BED2 | 7 | 18
Occupancy: | [6 empty] | PASSIVE 1.5ACH DSY1.aps | 005/3B5P/BED3 | 12 | PASSIVE 1.5ACH DSY1.aps | 005/3B5P/BED3 | 7 | 19
Note: | This report assesses occupied periods only. Please be aware that TM52 should be conducted for occupied and/or “available hours”. | [5 empty] | PASSIVE 1.5ACH DSY1.aps | 006/3B5P/BED1 | 8 | PASSIVE 1.5ACH DSY1.aps | 006/3B5P/BED1 | 6 | 14
| Use of educational NCM profiles may be seen as inappropriate due to prolonged unoccupied periods during summer months. | [5 empty] | PASSIVE 1.5ACH DSY1.aps | 006/3B5P/BED2 | 9 | PASSIVE 1.5ACH DSY1.aps | 006/3B5P/BED2 | 6 | 15
| See Section 6.1.2 (a) of TM52 for further information. | [5 empty] | PASSIVE 1.5ACH DSY1.aps | 006/3B5P/BED3 | 12 | PASSIVE 1.5ACH DSY1.aps | 006/3B5P/BED3 | 7 | 19
[7 empty] | PASSIVE 1.5ACH DSY1.aps | 007/1B2P/BED | 7 | PASSIVE 1.5ACH DSY1.aps | 007/1B2P/BED | 4 | 11
Passed: | 64 rooms: | [5 empty] | PASSIVE 1.5ACH DSY1.aps | 008/1B2P/BED | 8 | PASSIVE 1.5ACH DSY1.aps | 008/1B2P/BED | 6 | 14
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing | PASSIVE 1.5ACH DSY1.aps | 009/4B6P/BED1 | 12 | PASSIVE 1.5ACH DSY1.aps | 009/4B6P/BED1 | 6 | 18
001/1B2P/BED | 2 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY1.aps | 009/4B6P/BED2 | 7 | PASSIVE 1.5ACH DSY1.aps | 009/4B6P/BED2 | 2 | 9
001/1B2P/LDK | 0 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY1.aps | 009/4B6P/BED3 | 8 | PASSIVE 1.5ACH DSY1.aps | 009/4B6P/BED3 | 3 | 11
002/1B2P/BED | 7 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY1.aps | 009/4B6P/BED4 | 12 | PASSIVE 1.5ACH DSY1.aps | 009/4B6P/BED4 | 7 | 19
002/1B2P/LDK | 5 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY1.aps | 010/4B6P/BED1 | 12 | PASSIVE 1.5ACH DSY1.aps | 010/4B6P/BED1 | 7 | 19
003/3B5P/BED1 | 0000005A | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY1.aps | 010/4B6P/BED2 | 7 | PASSIVE 1.5ACH DSY1.aps | 010/4B6P/BED2 | 3 | 10
003/3B5P/BED2 | 0000005B | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY1.aps | 010/4B6P/BED3 | 7 | PASSIVE 1.5ACH DSY1.aps | 010/4B6P/BED3 | 3 | 10
003/3B5P/BED3 | 0000005C | 100 | 0.2 | 6 | 1 | - | PASSIVE 1.5ACH DSY1.aps | 010/4B6P/BED4 | 12 | PASSIVE 1.5ACH DSY1.aps | 010/4B6P/BED4 | 7 | 19
003/3B5P/DINKIT | 0000000D | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY1.aps | 011/2B4P/BED1 | 7 | PASSIVE 1.5ACH DSY1.aps | 011/2B4P/BED1 | 4 | 11
003/3B5P/LIV | 0000000C | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY1.aps | 011/2B4P/BED2 | 7 | PASSIVE 1.5ACH DSY1.aps | 011/2B4P/BED2 | 4 | 11
004/3B5P/BED1 | 62 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY1.aps | 012/2B4P/BED1 | 7 | PASSIVE 1.5ACH DSY1.aps | 012/2B4P/BED1 | 4 | 11
004/3B5P/BED2 | 63 | 100 | 0.1 | 4 | 1 | - | PASSIVE 1.5ACH DSY1.aps | 012/2B4P/BED2 | 8 | PASSIVE 1.5ACH DSY1.aps | 012/2B4P/BED2 | 4 | 12
004/3B5P/BED3 | 64 | 100 | 0.3 | 7 | 1 | 2 | PASSIVE 1.5ACH DSY1.aps | 013/2B4P/BED1 | 7 | PASSIVE 1.5ACH DSY1.aps | 013/2B4P/BED1 | 4 | 11
004/3B5P/DINKIT | 19 | 100 | 0.1 | 1 | 1 | - | PASSIVE 1.5ACH DSY1.aps | 013/2B4P/BED2 | 8 | PASSIVE 1.5ACH DSY1.aps | 013/2B4P/BED2 | 4 | 12
004/3B5P/LIV | 18 | 100 | 0.2 | 3 | 1 | - | PASSIVE 1.5ACH DSY1.aps | 014/2B4P/BED1 | 8 | PASSIVE 1.5ACH DSY1.aps | 014/2B4P/BED1 | 4 | 12
005/3B5P/BED1 | 69 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY1.aps | 014/2B4P/BED2 | 8 | PASSIVE 1.5ACH DSY1.aps | 014/2B4P/BED2 | 4 | 12
005/3B5P/BED2 | 0000006A | 100 | 0.1 | 3 | 1 | - | PASSIVE 1.5ACH DSY1.aps | 015/2B4P/BED1 | 8 | PASSIVE 1.5ACH DSY1.aps | 015/2B4P/BED1 | 5 | 13
005/3B5P/BED3 | 0000006B | 100 | 0.3 | 7 | 1 | 2 | PASSIVE 1.5ACH DSY1.aps | 015/2B4P/BED2 | 8 | PASSIVE 1.5ACH DSY1.aps | 015/2B4P/BED2 | 6 | 14
005/3B5P/DINKIT | 0000001A | 100 | 0.1 | 1 | 1 | - | PASSIVE 1.5ACH DSY1.aps | 016/2B4P/BED1 | 8 | PASSIVE 1.5ACH DSY1.aps | 016/2B4P/BED1 | 5 | 13
005/3B5P/LIV | 0000001B | 100 | 0.2 | 3 | 1 | - | PASSIVE 1.5ACH DSY1.aps | 016/2B4P/BED2 | 8 | PASSIVE 1.5ACH DSY1.aps | 016/2B4P/BED2 | 5 | 13
006/3B5P/BED1 | 71 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY1.aps | 017/2B4P/BED1 | 8 | PASSIVE 1.5ACH DSY1.aps | 017/2B4P/BED1 | 5 | 13
006/3B5P/BED2 | 70 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY1.aps | 017/2B4P/BED2 | 8 | PASSIVE 1.5ACH DSY1.aps | 017/2B4P/BED2 | 6 | 14
006/3B5P/BED3 | 0000006F | 100 | 0.2 | 5 | 1 | - | PASSIVE 1.5ACH DSY1.aps | 018/2B4P/BED1 | 8 | PASSIVE 1.5ACH DSY1.aps | 018/2B4P/BED1 | 6 | 14
006/3B5P/DINKIT | 27 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY1.aps | 018/2B4P/BED2 | 8 | PASSIVE 1.5ACH DSY1.aps | 018/2B4P/BED2 | 6 | 14
006/3B5P/LIV | 26 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY1.aps | Total hours | 352 | PASSIVE 1.5ACH DSY1.aps | Total hours | 214
007/1B2P/BED | 29 | 100 | 0 | 0 | 0 | -
007/1B2P/LDK | 28 | 100 | 0 | 0 | 0 | -
008/1B2P/BED | 31 | 100 | 0 | 0 | 0 | -
008/1B2P/LDK | 30 | 100 | 0 | 0 | 0 | -
009/4B6P/BED1 | 76 | 100 | 0.2 | 5 | 1 | -
009/4B6P/BED2 | 77 | 100 | 0 | 0 | 0 | -
009/4B6P/BED3 | 78 | 100 | 0 | 0 | 0 | -
009/4B6P/BED4 | 79 | 100 | 0.3 | 7 | 1 | 2
009/4B6P/DINKIT | 0000003D | 100 | 0 | 0 | 0 | -
009/4B6P/LIV | 0000003C | 100 | 0.1 | 1 | 1 | -
010/4B6P/BED1 | 1000026 | 100 | 0.3 | 6 | 1 | -
010/4B6P/BED2 | 1000027 | 100 | 0 | 0 | 0 | -
010/4B6P/BED3 | 1000028 | 100 | 0 | 0 | 0 | -
010/4B6P/BED4 | 1000029 | 100 | 0.3 | 7 | 1 | 2
010/4B6P/DINKIT | 1000006 | 100 | 0 | 0 | 0 | -
010/4B6P/LIV | 1000005 | 100 | 0.2 | 4 | 1 | -
011/2B4P/BED1 | 1000009 | 100 | 0 | 0 | 0 | -
011/2B4P/BED2 | 0100000A | 100 | 0 | 0 | 0 | -
011/2B4P/LDK | 1000008 | 100 | 0 | 0 | 0 | -
012/2B4P/BED1 | 1000011 | 100 | 0 | 0 | 0 | -
012/2B4P/BED2 | 1000012 | 100 | 0 | 0 | 0 | -
012/2B4P/LDK | 1000010 | 100 | 0 | 0 | 0 | -
013/2B4P/BED1 | 1000017 | 100 | 0 | 0 | 0 | -
013/2B4P/BED2 | 1000018 | 100 | 0 | 0 | 0 | -
013/2B4P/LDK | 1000016 | 100 | 0 | 0 | 0 | -
014/2B4P/BED1 | 1000020 | 100 | 0 | 0 | 0 | -
014/2B4P/BED2 | 1000021 | 100 | 0 | 0 | 0 | -
014/2B4P/LDK | 0100001F | 100 | 0 | 0 | 0 | -
015/2B4P/BED1 | 0100002D | 100 | 0 | 0 | 0 | -
015/2B4P/BED2 | 0100002E | 100 | 0 | 0 | 0 | -
015/2B4P/LDK | 1000031 | 100 | 0 | 0 | 0 | -
016/2B4P/BED1 | 1000034 | 100 | 0 | 0 | 0 | -
016/2B4P/BED2 | 1000035 | 100 | 0 | 0 | 0 | -
016/2B4P/LDK | 1000038 | 100 | 0 | 0 | 0 | -
017/2B4P/BED1 | 0100003B | 100 | 0 | 0 | 0 | -
017/2B4P/BED2 | 0100003C | 100 | 0 | 0 | 0 | -
017/2B4P/LDK | 0100003A | 100 | 0.1 | 1 | 1 | -
018/2B4P/BED1 | 1000044 | 100 | 0 | 0 | 0 | -
018/2B4P/BED2 | 1000045 | 100 | 0 | 0 | 0 | -
018/2B4P/LDK | 1000043 | 100 | 0.1 | 1 | 1 | -
Failed: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Unoccupied: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Note: | A TM 52 2013 analysis provides an assessment of comfort compliance based on bulk air modelling
i.e. each space is considered idealised and the air in the space perfectly mixed. The assessment does
not assess placement of space features e.g. windows & openings, airflow patterns or discomfort issues.
The user should assess these design aspects outside of the TM52 analysis.

## PASSIVE 1.5ACH DSY2_TM52
Overall | [8 empty] | Operative temperature (TM 52/CIBSE) (°C) - hours in range |  |  | Operative temperature (TM 52/CIBSE) (°C) - hours in range
Passed: | 64 rooms: | [5 empty] | File | Location | > 26.10 | File | Location | > 26.10
Failed: | 0 rooms: | [5 empty] | PASSIVE 1.5ACH DSY2.aps | 001/1B2P/BED | 18 | PASSIVE 1.5ACH DSY2.aps | 001/1B2P/BED | 32 | 50
Unoccupied: | 0 rooms: | [5 empty] | PASSIVE 1.5ACH DSY2.aps | 002/1B2P/BED | 17 | PASSIVE 1.5ACH DSY2.aps | 002/1B2P/BED | 27 | 44
[7 empty] | PASSIVE 1.5ACH DSY2.aps | 003/3B5P/BED1 | 17 | PASSIVE 1.5ACH DSY2.aps | 003/3B5P/BED1 | 32 | 49
Data: | [6 empty] | PASSIVE 1.5ACH DSY2.aps | 003/3B5P/BED2 | 19 | PASSIVE 1.5ACH DSY2.aps | 003/3B5P/BED2 | 28 | 47
Building category: | Category II (new builds.) | [5 empty] | PASSIVE 1.5ACH DSY2.aps | 003/3B5P/BED3 | 20 | PASSIVE 1.5ACH DSY2.aps | 003/3B5P/BED3 | 29 | 49
Weather file: | London_LWC_DSY2_2020High50.epw | [5 empty] | PASSIVE 1.5ACH DSY2.aps | 004/3B5P/BED1 | 18 | PASSIVE 1.5ACH DSY2.aps | 004/3B5P/BED1 | 30 | 48
Days data= | 365 | 2021-01-01 | 2021-12-31 |  |  |  | PASSIVE 1.5ACH DSY2.aps | 004/3B5P/BED2 | 20 | PASSIVE 1.5ACH DSY2.aps | 004/3B5P/BED2 | 33 | 53
Days (summer)= | 153 | 2021-05-01 | 2021-09-30 |  |  |  | PASSIVE 1.5ACH DSY2.aps | 004/3B5P/BED3 | 20 | PASSIVE 1.5ACH DSY2.aps | 004/3B5P/BED3 | 31 | 51
Data OK? | OK | Full summer |  |  |  |  | PASSIVE 1.5ACH DSY2.aps | 005/3B5P/BED1 | 18 | PASSIVE 1.5ACH DSY2.aps | 005/3B5P/BED1 | 30 | 48
[7 empty] | PASSIVE 1.5ACH DSY2.aps | 005/3B5P/BED2 | 20 | PASSIVE 1.5ACH DSY2.aps | 005/3B5P/BED2 | 33 | 53
Occupancy: | [6 empty] | PASSIVE 1.5ACH DSY2.aps | 005/3B5P/BED3 | 20 | PASSIVE 1.5ACH DSY2.aps | 005/3B5P/BED3 | 31 | 51
Note: | This report assesses occupied periods only. Please be aware that TM52 should be conducted for occupied and/or “available hours”. | [5 empty] | PASSIVE 1.5ACH DSY2.aps | 006/3B5P/BED1 | 17 | PASSIVE 1.5ACH DSY2.aps | 006/3B5P/BED1 | 32 | 49
| Use of educational NCM profiles may be seen as inappropriate due to prolonged unoccupied periods during summer months. | [5 empty] | PASSIVE 1.5ACH DSY2.aps | 006/3B5P/BED2 | 18 | PASSIVE 1.5ACH DSY2.aps | 006/3B5P/BED2 | 28 | 46
| See Section 6.1.2 (a) of TM52 for further information. | [5 empty] | PASSIVE 1.5ACH DSY2.aps | 006/3B5P/BED3 | 20 | PASSIVE 1.5ACH DSY2.aps | 006/3B5P/BED3 | 30 | 50
[7 empty] | PASSIVE 1.5ACH DSY2.aps | 007/1B2P/BED | 17 | PASSIVE 1.5ACH DSY2.aps | 007/1B2P/BED | 27 | 44
Passed: | 64 rooms: | [5 empty] | PASSIVE 1.5ACH DSY2.aps | 008/1B2P/BED | 18 | PASSIVE 1.5ACH DSY2.aps | 008/1B2P/BED | 36 | 54
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing | PASSIVE 1.5ACH DSY2.aps | 009/4B6P/BED1 | 20 | PASSIVE 1.5ACH DSY2.aps | 009/4B6P/BED1 | 27 | 47
001/1B2P/BED | 2 | 100 | 0.1 | 5 | 1 | - | PASSIVE 1.5ACH DSY2.aps | 009/4B6P/BED2 | 16 | PASSIVE 1.5ACH DSY2.aps | 009/4B6P/BED2 | 15 | 31
001/1B2P/LDK | 0 | 100 | 0.7 | 14 | 2 | 2 | PASSIVE 1.5ACH DSY2.aps | 009/4B6P/BED3 | 16 | PASSIVE 1.5ACH DSY2.aps | 009/4B6P/BED3 | 19 | 35
002/1B2P/BED | 7 | 100 | 0.1 | 5 | 1 | - | PASSIVE 1.5ACH DSY2.aps | 009/4B6P/BED4 | 20 | PASSIVE 1.5ACH DSY2.aps | 009/4B6P/BED4 | 29 | 49
002/1B2P/LDK | 5 | 100 | 0.4 | 6 | 2 | - | PASSIVE 1.5ACH DSY2.aps | 010/4B6P/BED1 | 20 | PASSIVE 1.5ACH DSY2.aps | 010/4B6P/BED1 | 27 | 47
003/3B5P/BED1 | 0000005A | 100 | 0.6 | 14 | 2 | 2 | PASSIVE 1.5ACH DSY2.aps | 010/4B6P/BED2 | 17 | PASSIVE 1.5ACH DSY2.aps | 010/4B6P/BED2 | 16 | 33
003/3B5P/BED2 | 0000005B | 100 | 0.9 | 21 | 3 | 2 | PASSIVE 1.5ACH DSY2.aps | 010/4B6P/BED3 | 17 | PASSIVE 1.5ACH DSY2.aps | 010/4B6P/BED3 | 15 | 32
003/3B5P/BED3 | 0000005C | 100 | 1.1 | 29 | 4 | 2 | PASSIVE 1.5ACH DSY2.aps | 010/4B6P/BED4 | 20 | PASSIVE 1.5ACH DSY2.aps | 010/4B6P/BED4 | 31 | 51
003/3B5P/DINKIT | 0000000D | 100 | 1.1 | 16 | 3 | 2 | PASSIVE 1.5ACH DSY2.aps | 011/2B4P/BED1 | 17 | PASSIVE 1.5ACH DSY2.aps | 011/2B4P/BED1 | 24 | 41
003/3B5P/LIV | 0000000C | 100 | 1.4 | 15 | 3 | 2 | PASSIVE 1.5ACH DSY2.aps | 011/2B4P/BED2 | 17 | PASSIVE 1.5ACH DSY2.aps | 011/2B4P/BED2 | 24 | 41
004/3B5P/BED1 | 62 | 100 | 0.9 | 20 | 3 | 2 | PASSIVE 1.5ACH DSY2.aps | 012/2B4P/BED1 | 17 | PASSIVE 1.5ACH DSY2.aps | 012/2B4P/BED1 | 24 | 41
004/3B5P/BED2 | 63 | 100 | 1.1 | 24 | 4 | 2 | PASSIVE 1.5ACH DSY2.aps | 012/2B4P/BED2 | 17 | PASSIVE 1.5ACH DSY2.aps | 012/2B4P/BED2 | 21 | 38
004/3B5P/BED3 | 64 | 100 | 1.1 | 30 | 4 | 2 | PASSIVE 1.5ACH DSY2.aps | 013/2B4P/BED1 | 17 | PASSIVE 1.5ACH DSY2.aps | 013/2B4P/BED1 | 24 | 41
004/3B5P/DINKIT | 19 | 100 | 1.5 | 21 | 3 | 2 | PASSIVE 1.5ACH DSY2.aps | 013/2B4P/BED2 | 17 | PASSIVE 1.5ACH DSY2.aps | 013/2B4P/BED2 | 21 | 38
004/3B5P/LIV | 18 | 100 | 1.6 | 22 | 3 | 2 | PASSIVE 1.5ACH DSY2.aps | 014/2B4P/BED1 | 17 | PASSIVE 1.5ACH DSY2.aps | 014/2B4P/BED1 | 27 | 44
005/3B5P/BED1 | 69 | 100 | 0.9 | 20 | 3 | 2 | PASSIVE 1.5ACH DSY2.aps | 014/2B4P/BED2 | 17 | PASSIVE 1.5ACH DSY2.aps | 014/2B4P/BED2 | 26 | 43
005/3B5P/BED2 | 0000006A | 100 | 1.1 | 24 | 4 | 2 | PASSIVE 1.5ACH DSY2.aps | 015/2B4P/BED1 | 17 | PASSIVE 1.5ACH DSY2.aps | 015/2B4P/BED1 | 28 | 45
005/3B5P/BED3 | 0000006B | 100 | 1.1 | 30 | 4 | 2 | PASSIVE 1.5ACH DSY2.aps | 015/2B4P/BED2 | 17 | PASSIVE 1.5ACH DSY2.aps | 015/2B4P/BED2 | 29 | 46
005/3B5P/DINKIT | 0000001A | 100 | 1.5 | 21 | 3 | 2 | PASSIVE 1.5ACH DSY2.aps | 016/2B4P/BED1 | 17 | PASSIVE 1.5ACH DSY2.aps | 016/2B4P/BED1 | 28 | 45
005/3B5P/LIV | 0000001B | 100 | 1.6 | 22 | 3 | 2 | PASSIVE 1.5ACH DSY2.aps | 016/2B4P/BED2 | 17 | PASSIVE 1.5ACH DSY2.aps | 016/2B4P/BED2 | 29 | 46
006/3B5P/BED1 | 71 | 100 | 0.6 | 14 | 2 | 2 | PASSIVE 1.5ACH DSY2.aps | 017/2B4P/BED1 | 17 | PASSIVE 1.5ACH DSY2.aps | 017/2B4P/BED1 | 28 | 45
006/3B5P/BED2 | 70 | 100 | 0.9 | 21 | 3 | 2 | PASSIVE 1.5ACH DSY2.aps | 017/2B4P/BED2 | 17 | PASSIVE 1.5ACH DSY2.aps | 017/2B4P/BED2 | 29 | 46
006/3B5P/BED3 | 0000006F | 100 | 1.1 | 29 | 4 | 2 | PASSIVE 1.5ACH DSY2.aps | 018/2B4P/BED1 | 17 | PASSIVE 1.5ACH DSY2.aps | 018/2B4P/BED1 | 31 | 48
006/3B5P/DINKIT | 27 | 100 | 1.2 | 15 | 3 | 2 | PASSIVE 1.5ACH DSY2.aps | 018/2B4P/BED2 | 17 | PASSIVE 1.5ACH DSY2.aps | 018/2B4P/BED2 | 31 | 48
006/3B5P/LIV | 26 | 100 | 1.4 | 15 | 3 | 2 | PASSIVE 1.5ACH DSY2.aps | Total hours | 715 | PASSIVE 1.5ACH DSY2.aps | Total hours | 1092
007/1B2P/BED | 29 | 100 | 0.1 | 5 | 1 | -
007/1B2P/LDK | 28 | 100 | 0.4 | 6 | 2 | -
008/1B2P/BED | 31 | 100 | 0.2 | 6 | 1 | -
008/1B2P/LDK | 30 | 100 | 1.1 | 15 | 2 | 2
009/4B6P/BED1 | 76 | 100 | 1 | 22 | 3 | 2
009/4B6P/BED2 | 77 | 100 | 0.7 | 14 | 2 | 2
009/4B6P/BED3 | 78 | 100 | 0.9 | 21 | 3 | 2
009/4B6P/BED4 | 79 | 100 | 1.1 | 28 | 4 | 2
009/4B6P/DINKIT | 0000003D | 100 | 0.9 | 13 | 2 | 2
009/4B6P/LIV | 0000003C | 100 | 1.6 | 21 | 3 | 2
010/4B6P/BED1 | 1000026 | 100 | 1 | 23 | 4 | 2
010/4B6P/BED2 | 1000027 | 100 | 0.7 | 15 | 2 | 2
010/4B6P/BED3 | 1000028 | 100 | 0.8 | 21 | 3 | 2
010/4B6P/BED4 | 1000029 | 100 | 1.2 | 30 | 4 | 2
010/4B6P/DINKIT | 1000006 | 100 | 1.3 | 18 | 3 | 2
010/4B6P/LIV | 1000005 | 100 | 1.8 | 25 | 4 | 2
011/2B4P/BED1 | 1000009 | 100 | 0.1 | 5 | 1 | -
011/2B4P/BED2 | 0100000A | 100 | 0.2 | 6 | 1 | -
011/2B4P/LDK | 1000008 | 100 | 0.7 | 13 | 2 | 2
012/2B4P/BED1 | 1000011 | 100 | 0.1 | 5 | 1 | -
012/2B4P/BED2 | 1000012 | 100 | 0.2 | 7 | 2 | 2
012/2B4P/LDK | 1000010 | 100 | 0.6 | 8 | 2 | 2
013/2B4P/BED1 | 1000017 | 100 | 0.1 | 5 | 1 | -
013/2B4P/BED2 | 1000018 | 100 | 0.2 | 8 | 2 | 2
013/2B4P/LDK | 1000016 | 100 | 0.7 | 10 | 2 | 2
014/2B4P/BED1 | 1000020 | 100 | 0.2 | 6 | 1 | -
014/2B4P/BED2 | 1000021 | 100 | 0.2 | 8 | 1 | 2
014/2B4P/LDK | 0100001F | 100 | 0.6 | 8 | 2 | 2
015/2B4P/BED1 | 0100002D | 100 | 0.2 | 6 | 1 | -
015/2B4P/BED2 | 0100002E | 100 | 0.6 | 15 | 2 | 2
015/2B4P/LDK | 1000031 | 100 | 1.3 | 19 | 3 | 2
016/2B4P/BED1 | 1000034 | 100 | 0.2 | 6 | 1 | -
016/2B4P/BED2 | 1000035 | 100 | 0.4 | 13 | 2 | 2
016/2B4P/LDK | 1000038 | 100 | 1.3 | 17 | 3 | 2
017/2B4P/BED1 | 0100003B | 100 | 0.2 | 7 | 1 | 2
017/2B4P/BED2 | 0100003C | 100 | 0.4 | 13 | 2 | 2
017/2B4P/LDK | 0100003A | 100 | 1.4 | 19 | 3 | 2
018/2B4P/BED1 | 1000044 | 100 | 0.2 | 9 | 2 | 2
018/2B4P/BED2 | 1000045 | 100 | 0.7 | 16 | 2 | 2
018/2B4P/LDK | 1000043 | 100 | 1.5 | 21 | 3 | 2
Failed: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Unoccupied: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Note: | A TM 52 2013 analysis provides an assessment of comfort compliance based on bulk air modelling
i.e. each space is considered idealised and the air in the space perfectly mixed. The assessment does
not assess placement of space features e.g. windows & openings, airflow patterns or discomfort issues.
The user should assess these design aspects outside of the TM52 analysis.

## PASSIVE 1.5ACH DSY3_TM52
Overall | [8 empty] | Operative temperature (TM 52/CIBSE) (°C) - hours in range |  |  | Operative temperature (TM 52/CIBSE) (°C) - hours in range
Passed: | 64 rooms: | [5 empty] | File | Location | > 26.10 | File | Location | > 26.10
Failed: | 0 rooms: | [5 empty] | PASSIVE 1.5ACH DSY3.aps | 001/1B2P/BED | 22 | PASSIVE 1.5ACH DSY3.aps | 001/1B2P/BED | 21 | 43
Unoccupied: | 0 rooms: | [5 empty] | PASSIVE 1.5ACH DSY3.aps | 002/1B2P/BED | 22 | PASSIVE 1.5ACH DSY3.aps | 002/1B2P/BED | 17 | 39
[7 empty] | PASSIVE 1.5ACH DSY3.aps | 003/3B5P/BED1 | 21 | PASSIVE 1.5ACH DSY3.aps | 003/3B5P/BED1 | 21 | 42
Data: | [6 empty] | PASSIVE 1.5ACH DSY3.aps | 003/3B5P/BED2 | 21 | PASSIVE 1.5ACH DSY3.aps | 003/3B5P/BED2 | 21 | 42
Building category: | Category II (new builds.) | [5 empty] | PASSIVE 1.5ACH DSY3.aps | 003/3B5P/BED3 | 22 | PASSIVE 1.5ACH DSY3.aps | 003/3B5P/BED3 | 21 | 43
Weather file: | London_LWC_DSY3_2020High50.epw | [5 empty] | PASSIVE 1.5ACH DSY3.aps | 004/3B5P/BED1 | 22 | PASSIVE 1.5ACH DSY3.aps | 004/3B5P/BED1 | 22 | 44
Days data= | 365 | 2021-01-01 | 2021-12-31 |  |  |  | PASSIVE 1.5ACH DSY3.aps | 004/3B5P/BED2 | 22 | PASSIVE 1.5ACH DSY3.aps | 004/3B5P/BED2 | 23 | 45
Days (summer)= | 153 | 2021-05-01 | 2021-09-30 |  |  |  | PASSIVE 1.5ACH DSY3.aps | 004/3B5P/BED3 | 22 | PASSIVE 1.5ACH DSY3.aps | 004/3B5P/BED3 | 24 | 46
Data OK? | OK | Full summer |  |  |  |  | PASSIVE 1.5ACH DSY3.aps | 005/3B5P/BED1 | 22 | PASSIVE 1.5ACH DSY3.aps | 005/3B5P/BED1 | 22 | 44
[7 empty] | PASSIVE 1.5ACH DSY3.aps | 005/3B5P/BED2 | 22 | PASSIVE 1.5ACH DSY3.aps | 005/3B5P/BED2 | 23 | 45
Occupancy: | [6 empty] | PASSIVE 1.5ACH DSY3.aps | 005/3B5P/BED3 | 22 | PASSIVE 1.5ACH DSY3.aps | 005/3B5P/BED3 | 24 | 46
Note: | This report assesses occupied periods only. Please be aware that TM52 should be conducted for occupied and/or “available hours”. | [5 empty] | PASSIVE 1.5ACH DSY3.aps | 006/3B5P/BED1 | 22 | PASSIVE 1.5ACH DSY3.aps | 006/3B5P/BED1 | 21 | 43
| Use of educational NCM profiles may be seen as inappropriate due to prolonged unoccupied periods during summer months. | [5 empty] | PASSIVE 1.5ACH DSY3.aps | 006/3B5P/BED2 | 21 | PASSIVE 1.5ACH DSY3.aps | 006/3B5P/BED2 | 20 | 41
| See Section 6.1.2 (a) of TM52 for further information. | [5 empty] | PASSIVE 1.5ACH DSY3.aps | 006/3B5P/BED3 | 22 | PASSIVE 1.5ACH DSY3.aps | 006/3B5P/BED3 | 21 | 43
[7 empty] | PASSIVE 1.5ACH DSY3.aps | 007/1B2P/BED | 21 | PASSIVE 1.5ACH DSY3.aps | 007/1B2P/BED | 17 | 38
Passed: | 64 rooms: | [5 empty] | PASSIVE 1.5ACH DSY3.aps | 008/1B2P/BED | 22 | PASSIVE 1.5ACH DSY3.aps | 008/1B2P/BED | 23 | 45
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing | PASSIVE 1.5ACH DSY3.aps | 009/4B6P/BED1 | 22 | PASSIVE 1.5ACH DSY3.aps | 009/4B6P/BED1 | 19 | 41
001/1B2P/BED | 2 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY3.aps | 009/4B6P/BED2 | 18 | PASSIVE 1.5ACH DSY3.aps | 009/4B6P/BED2 | 11 | 29
001/1B2P/LDK | 0 | 100 | 0.3 | 2 | 1 | - | PASSIVE 1.5ACH DSY3.aps | 009/4B6P/BED3 | 19 | PASSIVE 1.5ACH DSY3.aps | 009/4B6P/BED3 | 15 | 34
002/1B2P/BED | 7 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5ACH DSY3.aps | 009/4B6P/BED4 | 22 | PASSIVE 1.5ACH DSY3.aps | 009/4B6P/BED4 | 20 | 42
002/1B2P/LDK | 5 | 100 | 0.1 | 1 | 1 | - | PASSIVE 1.5ACH DSY3.aps | 010/4B6P/BED1 | 22 | PASSIVE 1.5ACH DSY3.aps | 010/4B6P/BED1 | 20 | 42
003/3B5P/BED1 | 0000005A | 100 | 0.6 | 8 | 1 | 2 | PASSIVE 1.5ACH DSY3.aps | 010/4B6P/BED2 | 18 | PASSIVE 1.5ACH DSY3.aps | 010/4B6P/BED2 | 12 | 30
003/3B5P/BED2 | 0000005B | 100 | 0.9 | 14 | 2 | 2 | PASSIVE 1.5ACH DSY3.aps | 010/4B6P/BED3 | 17 | PASSIVE 1.5ACH DSY3.aps | 010/4B6P/BED3 | 10 | 27
003/3B5P/BED3 | 0000005C | 100 | 1.1 | 20 | 2 | 2 | PASSIVE 1.5ACH DSY3.aps | 010/4B6P/BED4 | 22 | PASSIVE 1.5ACH DSY3.aps | 010/4B6P/BED4 | 24 | 46
003/3B5P/DINKIT | 0000000D | 100 | 0.7 | 6 | 1 | - | PASSIVE 1.5ACH DSY3.aps | 011/2B4P/BED1 | 19 | PASSIVE 1.5ACH DSY3.aps | 011/2B4P/BED1 | 16 | 35
003/3B5P/LIV | 0000000C | 100 | 1.2 | 8 | 1 | 2 | PASSIVE 1.5ACH DSY3.aps | 011/2B4P/BED2 | 19 | PASSIVE 1.5ACH DSY3.aps | 011/2B4P/BED2 | 16 | 35
004/3B5P/BED1 | 62 | 100 | 0.9 | 14 | 2 | 2 | PASSIVE 1.5ACH DSY3.aps | 012/2B4P/BED1 | 19 | PASSIVE 1.5ACH DSY3.aps | 012/2B4P/BED1 | 16 | 35
004/3B5P/BED2 | 63 | 100 | 1 | 18 | 2 | 2 | PASSIVE 1.5ACH DSY3.aps | 012/2B4P/BED2 | 19 | PASSIVE 1.5ACH DSY3.aps | 012/2B4P/BED2 | 16 | 35
004/3B5P/BED3 | 64 | 100 | 1.2 | 26 | 3 | 2 | PASSIVE 1.5ACH DSY3.aps | 013/2B4P/BED1 | 19 | PASSIVE 1.5ACH DSY3.aps | 013/2B4P/BED1 | 16 | 35
004/3B5P/DINKIT | 19 | 100 | 1.2 | 10 | 2 | 2 | PASSIVE 1.5ACH DSY3.aps | 013/2B4P/BED2 | 21 | PASSIVE 1.5ACH DSY3.aps | 013/2B4P/BED2 | 16 | 37
004/3B5P/LIV | 18 | 100 | 1.6 | 14 | 2 | 2 | PASSIVE 1.5ACH DSY3.aps | 014/2B4P/BED1 | 20 | PASSIVE 1.5ACH DSY3.aps | 014/2B4P/BED1 | 16 | 36
005/3B5P/BED1 | 69 | 100 | 0.9 | 14 | 2 | 2 | PASSIVE 1.5ACH DSY3.aps | 014/2B4P/BED2 | 20 | PASSIVE 1.5ACH DSY3.aps | 014/2B4P/BED2 | 16 | 36
005/3B5P/BED2 | 0000006A | 100 | 1 | 18 | 2 | 2 | PASSIVE 1.5ACH DSY3.aps | 015/2B4P/BED1 | 20 | PASSIVE 1.5ACH DSY3.aps | 015/2B4P/BED1 | 18 | 38
005/3B5P/BED3 | 0000006B | 100 | 1.2 | 26 | 3 | 2 | PASSIVE 1.5ACH DSY3.aps | 015/2B4P/BED2 | 20 | PASSIVE 1.5ACH DSY3.aps | 015/2B4P/BED2 | 19 | 39
005/3B5P/DINKIT | 0000001A | 100 | 1.2 | 10 | 2 | 2 | PASSIVE 1.5ACH DSY3.aps | 016/2B4P/BED1 | 20 | PASSIVE 1.5ACH DSY3.aps | 016/2B4P/BED1 | 18 | 38
005/3B5P/LIV | 0000001B | 100 | 1.6 | 13 | 2 | 2 | PASSIVE 1.5ACH DSY3.aps | 016/2B4P/BED2 | 20 | PASSIVE 1.5ACH DSY3.aps | 016/2B4P/BED2 | 19 | 39
006/3B5P/BED1 | 71 | 100 | 0.6 | 8 | 1 | 2 | PASSIVE 1.5ACH DSY3.aps | 017/2B4P/BED1 | 20 | PASSIVE 1.5ACH DSY3.aps | 017/2B4P/BED1 | 18 | 38
006/3B5P/BED2 | 70 | 100 | 0.9 | 13 | 2 | 2 | PASSIVE 1.5ACH DSY3.aps | 017/2B4P/BED2 | 21 | PASSIVE 1.5ACH DSY3.aps | 017/2B4P/BED2 | 19 | 40
006/3B5P/BED3 | 0000006F | 100 | 1.1 | 20 | 2 | 2 | PASSIVE 1.5ACH DSY3.aps | 018/2B4P/BED1 | 22 | PASSIVE 1.5ACH DSY3.aps | 018/2B4P/BED1 | 21 | 43
006/3B5P/DINKIT | 27 | 100 | 0.7 | 5 | 1 | - | PASSIVE 1.5ACH DSY3.aps | 018/2B4P/BED2 | 22 | PASSIVE 1.5ACH DSY3.aps | 018/2B4P/BED2 | 21 | 43
006/3B5P/LIV | 26 | 100 | 1.1 | 7 | 1 | 2 | PASSIVE 1.5ACH DSY3.aps | Total hours | 829 | PASSIVE 1.5ACH DSY3.aps | Total hours | 753
007/1B2P/BED | 29 | 100 | 0 | 0 | 0 | -
007/1B2P/LDK | 28 | 100 | 0.1 | 1 | 1 | -
008/1B2P/BED | 31 | 100 | 0 | 0 | 0 | -
008/1B2P/LDK | 30 | 100 | 0.5 | 5 | 1 | -
009/4B6P/BED1 | 76 | 100 | 1 | 20 | 2 | 2
009/4B6P/BED2 | 77 | 100 | 0.7 | 11 | 2 | 2
009/4B6P/BED3 | 78 | 100 | 0.9 | 15 | 2 | 2
009/4B6P/BED4 | 79 | 100 | 1.2 | 24 | 3 | 2
009/4B6P/DINKIT | 0000003D | 100 | 0.8 | 6 | 1 | -
009/4B6P/LIV | 0000003C | 100 | 1.5 | 13 | 2 | 2
010/4B6P/BED1 | 1000026 | 100 | 1.1 | 20 | 2 | 2
010/4B6P/BED2 | 1000027 | 100 | 0.8 | 10 | 2 | 2
010/4B6P/BED3 | 1000028 | 100 | 1 | 16 | 2 | 2
010/4B6P/BED4 | 1000029 | 100 | 1.3 | 26 | 3 | 2
010/4B6P/DINKIT | 1000006 | 100 | 1.3 | 10 | 2 | 2
010/4B6P/LIV | 1000005 | 100 | 1.7 | 16 | 2 | 2
011/2B4P/BED1 | 1000009 | 100 | 0 | 0 | 0 | -
011/2B4P/BED2 | 0100000A | 100 | 0 | 0 | 0 | -
011/2B4P/LDK | 1000008 | 100 | 0.4 | 3 | 1 | -
012/2B4P/BED1 | 1000011 | 100 | 0 | 0 | 0 | -
012/2B4P/BED2 | 1000012 | 100 | 0.1 | 2 | 1 | -
012/2B4P/LDK | 1000010 | 100 | 0.3 | 2 | 1 | -
013/2B4P/BED1 | 1000017 | 100 | 0 | 0 | 0 | -
013/2B4P/BED2 | 1000018 | 100 | 0.1 | 2 | 1 | -
013/2B4P/LDK | 1000016 | 100 | 0.5 | 3 | 1 | -
014/2B4P/BED1 | 1000020 | 100 | 0 | 0 | 0 | -
014/2B4P/BED2 | 1000021 | 100 | 0 | 0 | 0 | -
014/2B4P/LDK | 0100001F | 100 | 0.3 | 2 | 1 | -
015/2B4P/BED1 | 0100002D | 100 | 0 | 0 | 0 | -
015/2B4P/BED2 | 0100002E | 100 | 0.4 | 6 | 1 | -
015/2B4P/LDK | 1000031 | 100 | 1.3 | 10 | 2 | 2
016/2B4P/BED1 | 1000034 | 100 | 0 | 0 | 0 | -
016/2B4P/BED2 | 1000035 | 100 | 0.3 | 5 | 1 | -
016/2B4P/LDK | 1000038 | 100 | 1.2 | 10 | 2 | 2
017/2B4P/BED1 | 0100003B | 100 | 0 | 0 | 0 | -
017/2B4P/BED2 | 0100003C | 100 | 0.4 | 6 | 1 | -
017/2B4P/LDK | 0100003A | 100 | 1.2 | 10 | 2 | 2
018/2B4P/BED1 | 1000044 | 100 | 0 | 1 | 1 | -
018/2B4P/BED2 | 1000045 | 100 | 0.6 | 8 | 1 | 2
018/2B4P/LDK | 1000043 | 100 | 1.4 | 10 | 2 | 2
Failed: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Unoccupied: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Note: | A TM 52 2013 analysis provides an assessment of comfort compliance based on bulk air modelling
i.e. each space is considered idealised and the air in the space perfectly mixed. The assessment does
not assess placement of space features e.g. windows & openings, airflow patterns or discomfort issues.
The user should assess these design aspects outside of the TM52 analysis.

## PASSIVE 1.5KW DSY1_TM52
Overall | [8 empty] | Operative temperature (TM 52/CIBSE) (°C) - hours in range |  |  | Operative temperature (TM 52/CIBSE) (°C) - hours in range
Passed: | 64 rooms: | [5 empty] | File | Location | > 26.10 | File | Location | > 26.10
Failed: | 0 rooms: | [5 empty] | PASSIVE 1.5KW DSY1.aps | 001/1B2P/BED | 0 | PASSIVE 1.5KW DSY1.aps | 001/1B2P/BED | 0 | 0
Unoccupied: | 0 rooms: | [5 empty] | PASSIVE 1.5KW DSY1.aps | 002/1B2P/BED | 0 | PASSIVE 1.5KW DSY1.aps | 002/1B2P/BED | 0 | 0
[7 empty] | PASSIVE 1.5KW DSY1.aps | 003/3B5P/BED1 | 0 | PASSIVE 1.5KW DSY1.aps | 003/3B5P/BED1 | 0 | 0
Data: | [6 empty] | PASSIVE 1.5KW DSY1.aps | 003/3B5P/BED2 | 0 | PASSIVE 1.5KW DSY1.aps | 003/3B5P/BED2 | 0 | 0
Building category: | Category II (new builds.) | [5 empty] | PASSIVE 1.5KW DSY1.aps | 003/3B5P/BED3 | 0 | PASSIVE 1.5KW DSY1.aps | 003/3B5P/BED3 | 0 | 0
Weather file: | London_LWC_DSY1_2020High50.epw | [5 empty] | PASSIVE 1.5KW DSY1.aps | 004/3B5P/BED1 | 0 | PASSIVE 1.5KW DSY1.aps | 004/3B5P/BED1 | 0 | 0
Days data= | 365 | 2021-01-01 | 2021-12-31 |  |  |  | PASSIVE 1.5KW DSY1.aps | 004/3B5P/BED2 | 0 | PASSIVE 1.5KW DSY1.aps | 004/3B5P/BED2 | 0 | 0
Days (summer)= | 153 | 2021-05-01 | 2021-09-30 |  |  |  | PASSIVE 1.5KW DSY1.aps | 004/3B5P/BED3 | 0 | PASSIVE 1.5KW DSY1.aps | 004/3B5P/BED3 | 0 | 0
Data OK? | OK | Full summer |  |  |  |  | PASSIVE 1.5KW DSY1.aps | 005/3B5P/BED1 | 0 | PASSIVE 1.5KW DSY1.aps | 005/3B5P/BED1 | 0 | 0
[7 empty] | PASSIVE 1.5KW DSY1.aps | 005/3B5P/BED2 | 0 | PASSIVE 1.5KW DSY1.aps | 005/3B5P/BED2 | 0 | 0
Occupancy: | [6 empty] | PASSIVE 1.5KW DSY1.aps | 005/3B5P/BED3 | 0 | PASSIVE 1.5KW DSY1.aps | 005/3B5P/BED3 | 0 | 0
Note: | This report assesses occupied periods only. Please be aware that TM52 should be conducted for occupied and/or “available hours”. | [5 empty] | PASSIVE 1.5KW DSY1.aps | 006/3B5P/BED1 | 0 | PASSIVE 1.5KW DSY1.aps | 006/3B5P/BED1 | 0 | 0
| Use of educational NCM profiles may be seen as inappropriate due to prolonged unoccupied periods during summer months. | [5 empty] | PASSIVE 1.5KW DSY1.aps | 006/3B5P/BED2 | 0 | PASSIVE 1.5KW DSY1.aps | 006/3B5P/BED2 | 0 | 0
| See Section 6.1.2 (a) of TM52 for further information. | [5 empty] | PASSIVE 1.5KW DSY1.aps | 006/3B5P/BED3 | 0 | PASSIVE 1.5KW DSY1.aps | 006/3B5P/BED3 | 0 | 0
[7 empty] | PASSIVE 1.5KW DSY1.aps | 007/1B2P/BED | 0 | PASSIVE 1.5KW DSY1.aps | 007/1B2P/BED | 0 | 0
Passed: | 64 rooms: | [5 empty] | PASSIVE 1.5KW DSY1.aps | 008/1B2P/BED | 0 | PASSIVE 1.5KW DSY1.aps | 008/1B2P/BED | 0 | 0
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing | PASSIVE 1.5KW DSY1.aps | 009/4B6P/BED1 | 0 | PASSIVE 1.5KW DSY1.aps | 009/4B6P/BED1 | 0 | 0
001/1B2P/BED | 2 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 009/4B6P/BED2 | 0 | PASSIVE 1.5KW DSY1.aps | 009/4B6P/BED2 | 0 | 0
001/1B2P/LDK | 0 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 009/4B6P/BED3 | 0 | PASSIVE 1.5KW DSY1.aps | 009/4B6P/BED3 | 0 | 0
002/1B2P/BED | 7 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 009/4B6P/BED4 | 0 | PASSIVE 1.5KW DSY1.aps | 009/4B6P/BED4 | 0 | 0
002/1B2P/LDK | 5 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 010/4B6P/BED1 | 0 | PASSIVE 1.5KW DSY1.aps | 010/4B6P/BED1 | 0 | 0
003/3B5P/BED1 | 0000005A | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 010/4B6P/BED2 | 0 | PASSIVE 1.5KW DSY1.aps | 010/4B6P/BED2 | 0 | 0
003/3B5P/BED2 | 0000005B | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 010/4B6P/BED3 | 0 | PASSIVE 1.5KW DSY1.aps | 010/4B6P/BED3 | 0 | 0
003/3B5P/BED3 | 0000005C | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 010/4B6P/BED4 | 0 | PASSIVE 1.5KW DSY1.aps | 010/4B6P/BED4 | 0 | 0
003/3B5P/DINKIT | 0000000D | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 011/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY1.aps | 011/2B4P/BED1 | 0 | 0
003/3B5P/LIV | 0000000C | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 011/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY1.aps | 011/2B4P/BED2 | 0 | 0
004/3B5P/BED1 | 62 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 012/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY1.aps | 012/2B4P/BED1 | 0 | 0
004/3B5P/BED2 | 63 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 012/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY1.aps | 012/2B4P/BED2 | 0 | 0
004/3B5P/BED3 | 64 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 013/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY1.aps | 013/2B4P/BED1 | 0 | 0
004/3B5P/DINKIT | 19 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 013/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY1.aps | 013/2B4P/BED2 | 0 | 0
004/3B5P/LIV | 18 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 014/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY1.aps | 014/2B4P/BED1 | 0 | 0
005/3B5P/BED1 | 69 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 014/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY1.aps | 014/2B4P/BED2 | 0 | 0
005/3B5P/BED2 | 0000006A | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 015/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY1.aps | 015/2B4P/BED1 | 0 | 0
005/3B5P/BED3 | 0000006B | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 015/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY1.aps | 015/2B4P/BED2 | 0 | 0
005/3B5P/DINKIT | 0000001A | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 016/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY1.aps | 016/2B4P/BED1 | 0 | 0
005/3B5P/LIV | 0000001B | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 016/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY1.aps | 016/2B4P/BED2 | 0 | 0
006/3B5P/BED1 | 71 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 017/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY1.aps | 017/2B4P/BED1 | 0 | 0
006/3B5P/BED2 | 70 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 017/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY1.aps | 017/2B4P/BED2 | 0 | 0
006/3B5P/BED3 | 0000006F | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 018/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY1.aps | 018/2B4P/BED1 | 0 | 0
006/3B5P/DINKIT | 27 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | 018/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY1.aps | 018/2B4P/BED2 | 0 | 0
006/3B5P/LIV | 26 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY1.aps | Total hours | 0 | PASSIVE 1.5KW DSY1.aps | Total hours | 0
007/1B2P/BED | 29 | 100 | 0 | 0 | 0 | -
007/1B2P/LDK | 28 | 100 | 0 | 0 | 0 | -
008/1B2P/BED | 31 | 100 | 0 | 0 | 0 | -
008/1B2P/LDK | 30 | 100 | 0 | 0 | 0 | -
009/4B6P/BED1 | 76 | 100 | 0 | 0 | 0 | -
009/4B6P/BED2 | 77 | 100 | 0 | 0 | 0 | -
009/4B6P/BED3 | 78 | 100 | 0 | 0 | 0 | -
009/4B6P/BED4 | 79 | 100 | 0 | 0 | 0 | -
009/4B6P/DINKIT | 0000003D | 100 | 0 | 0 | 0 | -
009/4B6P/LIV | 0000003C | 100 | 0 | 0 | 0 | -
010/4B6P/BED1 | 1000026 | 100 | 0 | 0 | 0 | -
010/4B6P/BED2 | 1000027 | 100 | 0 | 0 | 0 | -
010/4B6P/BED3 | 1000028 | 100 | 0 | 0 | 0 | -
010/4B6P/BED4 | 1000029 | 100 | 0 | 0 | 0 | -
010/4B6P/DINKIT | 1000006 | 100 | 0 | 0 | 0 | -
010/4B6P/LIV | 1000005 | 100 | 0 | 0 | 0 | -
011/2B4P/BED1 | 1000009 | 100 | 0 | 0 | 0 | -
011/2B4P/BED2 | 0100000A | 100 | 0 | 0 | 0 | -
011/2B4P/LDK | 1000008 | 100 | 0 | 0 | 0 | -
012/2B4P/BED1 | 1000011 | 100 | 0 | 0 | 0 | -
012/2B4P/BED2 | 1000012 | 100 | 0 | 0 | 0 | -
012/2B4P/LDK | 1000010 | 100 | 0 | 0 | 0 | -
013/2B4P/BED1 | 1000017 | 100 | 0 | 0 | 0 | -
013/2B4P/BED2 | 1000018 | 100 | 0 | 0 | 0 | -
013/2B4P/LDK | 1000016 | 100 | 0 | 0 | 0 | -
014/2B4P/BED1 | 1000020 | 100 | 0 | 0 | 0 | -
014/2B4P/BED2 | 1000021 | 100 | 0 | 0 | 0 | -
014/2B4P/LDK | 0100001F | 100 | 0 | 0 | 0 | -
015/2B4P/BED1 | 0100002D | 100 | 0 | 0 | 0 | -
015/2B4P/BED2 | 0100002E | 100 | 0 | 0 | 0 | -
015/2B4P/LDK | 1000031 | 100 | 0 | 0 | 0 | -
016/2B4P/BED1 | 1000034 | 100 | 0 | 0 | 0 | -
016/2B4P/BED2 | 1000035 | 100 | 0 | 0 | 0 | -
016/2B4P/LDK | 1000038 | 100 | 0 | 0 | 0 | -
017/2B4P/BED1 | 0100003B | 100 | 0 | 0 | 0 | -
017/2B4P/BED2 | 0100003C | 100 | 0 | 0 | 0 | -
017/2B4P/LDK | 0100003A | 100 | 0 | 0 | 0 | -
018/2B4P/BED1 | 1000044 | 100 | 0 | 0 | 0 | -
018/2B4P/BED2 | 1000045 | 100 | 0 | 0 | 0 | -
018/2B4P/LDK | 1000043 | 100 | 0 | 0 | 0 | -
Failed: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Unoccupied: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Note: | A TM 52 2013 analysis provides an assessment of comfort compliance based on bulk air modelling
i.e. each space is considered idealised and the air in the space perfectly mixed. The assessment does
not assess placement of space features e.g. windows & openings, airflow patterns or discomfort issues.
The user should assess these design aspects outside of the TM52 analysis.

## PASSIVE 1.5KW DSY2_TM52
Overall | [8 empty] | Operative temperature (TM 52/CIBSE) (°C) - hours in range |  |  | Operative temperature (TM 52/CIBSE) (°C) - hours in range
Passed: | 64 rooms: | [5 empty] | File | Location | > 26.10 | File | Location | > 26.10
Failed: | 0 rooms: | [5 empty] | PASSIVE 1.5KW DSY2.aps | 001/1B2P/BED | 0 | PASSIVE 1.5KW DSY2.aps | 001/1B2P/BED | 0 | 0
Unoccupied: | 0 rooms: | [5 empty] | PASSIVE 1.5KW DSY2.aps | 002/1B2P/BED | 0 | PASSIVE 1.5KW DSY2.aps | 002/1B2P/BED | 0 | 0
[7 empty] | PASSIVE 1.5KW DSY2.aps | 003/3B5P/BED1 | 0 | PASSIVE 1.5KW DSY2.aps | 003/3B5P/BED1 | 0 | 0
Data: | [6 empty] | PASSIVE 1.5KW DSY2.aps | 003/3B5P/BED2 | 0 | PASSIVE 1.5KW DSY2.aps | 003/3B5P/BED2 | 0 | 0
Building category: | Category II (new builds.) | [5 empty] | PASSIVE 1.5KW DSY2.aps | 003/3B5P/BED3 | 0 | PASSIVE 1.5KW DSY2.aps | 003/3B5P/BED3 | 0 | 0
Weather file: | London_LWC_DSY2_2020High50.epw | [5 empty] | PASSIVE 1.5KW DSY2.aps | 004/3B5P/BED1 | 0 | PASSIVE 1.5KW DSY2.aps | 004/3B5P/BED1 | 0 | 0
Days data= | 365 | 2021-01-01 | 2021-12-31 |  |  |  | PASSIVE 1.5KW DSY2.aps | 004/3B5P/BED2 | 0 | PASSIVE 1.5KW DSY2.aps | 004/3B5P/BED2 | 0 | 0
Days (summer)= | 153 | 2021-05-01 | 2021-09-30 |  |  |  | PASSIVE 1.5KW DSY2.aps | 004/3B5P/BED3 | 0 | PASSIVE 1.5KW DSY2.aps | 004/3B5P/BED3 | 0 | 0
Data OK? | OK | Full summer |  |  |  |  | PASSIVE 1.5KW DSY2.aps | 005/3B5P/BED1 | 0 | PASSIVE 1.5KW DSY2.aps | 005/3B5P/BED1 | 0 | 0
[7 empty] | PASSIVE 1.5KW DSY2.aps | 005/3B5P/BED2 | 0 | PASSIVE 1.5KW DSY2.aps | 005/3B5P/BED2 | 0 | 0
Occupancy: | [6 empty] | PASSIVE 1.5KW DSY2.aps | 005/3B5P/BED3 | 0 | PASSIVE 1.5KW DSY2.aps | 005/3B5P/BED3 | 0 | 0
Note: | This report assesses occupied periods only. Please be aware that TM52 should be conducted for occupied and/or “available hours”. | [5 empty] | PASSIVE 1.5KW DSY2.aps | 006/3B5P/BED1 | 0 | PASSIVE 1.5KW DSY2.aps | 006/3B5P/BED1 | 0 | 0
| Use of educational NCM profiles may be seen as inappropriate due to prolonged unoccupied periods during summer months. | [5 empty] | PASSIVE 1.5KW DSY2.aps | 006/3B5P/BED2 | 0 | PASSIVE 1.5KW DSY2.aps | 006/3B5P/BED2 | 0 | 0
| See Section 6.1.2 (a) of TM52 for further information. | [5 empty] | PASSIVE 1.5KW DSY2.aps | 006/3B5P/BED3 | 0 | PASSIVE 1.5KW DSY2.aps | 006/3B5P/BED3 | 0 | 0
[7 empty] | PASSIVE 1.5KW DSY2.aps | 007/1B2P/BED | 0 | PASSIVE 1.5KW DSY2.aps | 007/1B2P/BED | 0 | 0
Passed: | 64 rooms: | [5 empty] | PASSIVE 1.5KW DSY2.aps | 008/1B2P/BED | 0 | PASSIVE 1.5KW DSY2.aps | 008/1B2P/BED | 0 | 0
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing | PASSIVE 1.5KW DSY2.aps | 009/4B6P/BED1 | 0 | PASSIVE 1.5KW DSY2.aps | 009/4B6P/BED1 | 0 | 0
001/1B2P/BED | 2 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 009/4B6P/BED2 | 0 | PASSIVE 1.5KW DSY2.aps | 009/4B6P/BED2 | 0 | 0
001/1B2P/LDK | 0 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 009/4B6P/BED3 | 0 | PASSIVE 1.5KW DSY2.aps | 009/4B6P/BED3 | 0 | 0
002/1B2P/BED | 7 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 009/4B6P/BED4 | 0 | PASSIVE 1.5KW DSY2.aps | 009/4B6P/BED4 | 0 | 0
002/1B2P/LDK | 5 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 010/4B6P/BED1 | 0 | PASSIVE 1.5KW DSY2.aps | 010/4B6P/BED1 | 0 | 0
003/3B5P/BED1 | 0000005A | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 010/4B6P/BED2 | 0 | PASSIVE 1.5KW DSY2.aps | 010/4B6P/BED2 | 0 | 0
003/3B5P/BED2 | 0000005B | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 010/4B6P/BED3 | 0 | PASSIVE 1.5KW DSY2.aps | 010/4B6P/BED3 | 0 | 0
003/3B5P/BED3 | 0000005C | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 010/4B6P/BED4 | 0 | PASSIVE 1.5KW DSY2.aps | 010/4B6P/BED4 | 0 | 0
003/3B5P/DINKIT | 0000000D | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 011/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY2.aps | 011/2B4P/BED1 | 0 | 0
003/3B5P/LIV | 0000000C | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 011/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY2.aps | 011/2B4P/BED2 | 0 | 0
004/3B5P/BED1 | 62 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 012/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY2.aps | 012/2B4P/BED1 | 0 | 0
004/3B5P/BED2 | 63 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 012/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY2.aps | 012/2B4P/BED2 | 0 | 0
004/3B5P/BED3 | 64 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 013/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY2.aps | 013/2B4P/BED1 | 0 | 0
004/3B5P/DINKIT | 19 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 013/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY2.aps | 013/2B4P/BED2 | 0 | 0
004/3B5P/LIV | 18 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 014/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY2.aps | 014/2B4P/BED1 | 0 | 0
005/3B5P/BED1 | 69 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 014/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY2.aps | 014/2B4P/BED2 | 0 | 0
005/3B5P/BED2 | 0000006A | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 015/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY2.aps | 015/2B4P/BED1 | 0 | 0
005/3B5P/BED3 | 0000006B | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 015/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY2.aps | 015/2B4P/BED2 | 0 | 0
005/3B5P/DINKIT | 0000001A | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 016/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY2.aps | 016/2B4P/BED1 | 0 | 0
005/3B5P/LIV | 0000001B | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 016/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY2.aps | 016/2B4P/BED2 | 0 | 0
006/3B5P/BED1 | 71 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 017/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY2.aps | 017/2B4P/BED1 | 0 | 0
006/3B5P/BED2 | 70 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 017/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY2.aps | 017/2B4P/BED2 | 0 | 0
006/3B5P/BED3 | 0000006F | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 018/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY2.aps | 018/2B4P/BED1 | 0 | 0
006/3B5P/DINKIT | 27 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | 018/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY2.aps | 018/2B4P/BED2 | 0 | 0
006/3B5P/LIV | 26 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY2.aps | Total hours | 0 | PASSIVE 1.5KW DSY2.aps | Total hours | 0
007/1B2P/BED | 29 | 100 | 0 | 0 | 0 | -
007/1B2P/LDK | 28 | 100 | 0 | 0 | 0 | -
008/1B2P/BED | 31 | 100 | 0 | 0 | 0 | -
008/1B2P/LDK | 30 | 100 | 0 | 0 | 0 | -
009/4B6P/BED1 | 76 | 100 | 0 | 0 | 0 | -
009/4B6P/BED2 | 77 | 100 | 0 | 0 | 0 | -
009/4B6P/BED3 | 78 | 100 | 0 | 0 | 0 | -
009/4B6P/BED4 | 79 | 100 | 0 | 0 | 0 | -
009/4B6P/DINKIT | 0000003D | 100 | 0 | 0 | 0 | -
009/4B6P/LIV | 0000003C | 100 | 0 | 0 | 0 | -
010/4B6P/BED1 | 1000026 | 100 | 0 | 0 | 0 | -
010/4B6P/BED2 | 1000027 | 100 | 0 | 0 | 0 | -
010/4B6P/BED3 | 1000028 | 100 | 0 | 0 | 0 | -
010/4B6P/BED4 | 1000029 | 100 | 0 | 0 | 0 | -
010/4B6P/DINKIT | 1000006 | 100 | 0 | 0 | 0 | -
010/4B6P/LIV | 1000005 | 100 | 0 | 0 | 0 | -
011/2B4P/BED1 | 1000009 | 100 | 0 | 0 | 0 | -
011/2B4P/BED2 | 0100000A | 100 | 0 | 0 | 0 | -
011/2B4P/LDK | 1000008 | 100 | 0 | 0 | 0 | -
012/2B4P/BED1 | 1000011 | 100 | 0 | 0 | 0 | -
012/2B4P/BED2 | 1000012 | 100 | 0 | 0 | 0 | -
012/2B4P/LDK | 1000010 | 100 | 0 | 0 | 0 | -
013/2B4P/BED1 | 1000017 | 100 | 0 | 0 | 0 | -
013/2B4P/BED2 | 1000018 | 100 | 0 | 0 | 0 | -
013/2B4P/LDK | 1000016 | 100 | 0 | 0 | 0 | -
014/2B4P/BED1 | 1000020 | 100 | 0 | 0 | 0 | -
014/2B4P/BED2 | 1000021 | 100 | 0 | 0 | 0 | -
014/2B4P/LDK | 0100001F | 100 | 0 | 0 | 0 | -
015/2B4P/BED1 | 0100002D | 100 | 0 | 0 | 0 | -
015/2B4P/BED2 | 0100002E | 100 | 0 | 0 | 0 | -
015/2B4P/LDK | 1000031 | 100 | 0 | 0 | 0 | -
016/2B4P/BED1 | 1000034 | 100 | 0 | 0 | 0 | -
016/2B4P/BED2 | 1000035 | 100 | 0 | 0 | 0 | -
016/2B4P/LDK | 1000038 | 100 | 0 | 0 | 0 | -
017/2B4P/BED1 | 0100003B | 100 | 0 | 0 | 0 | -
017/2B4P/BED2 | 0100003C | 100 | 0 | 0 | 0 | -
017/2B4P/LDK | 0100003A | 100 | 0 | 0 | 0 | -
018/2B4P/BED1 | 1000044 | 100 | 0 | 0 | 0 | -
018/2B4P/BED2 | 1000045 | 100 | 0 | 0 | 0 | -
018/2B4P/LDK | 1000043 | 100 | 0 | 0 | 0 | -
Failed: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Unoccupied: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Note: | A TM 52 2013 analysis provides an assessment of comfort compliance based on bulk air modelling
i.e. each space is considered idealised and the air in the space perfectly mixed. The assessment does
not assess placement of space features e.g. windows & openings, airflow patterns or discomfort issues.
The user should assess these design aspects outside of the TM52 analysis.

## PASSIVE 1.5KW DSY3_TM52
Overall | [8 empty] | Operative temperature (TM 52/CIBSE) (°C) - hours in range |  |  | Operative temperature (TM 52/CIBSE) (°C) - hours in range
Passed: | 64 rooms: | [5 empty] | File | Location | > 26.10 | File | Location | > 26.10
Failed: | 0 rooms: | [5 empty] | PASSIVE 1.5KW DSY3.aps | 001/1B2P/BED | 0 | PASSIVE 1.5KW DSY3.aps | 001/1B2P/BED | 0 | 0
Unoccupied: | 0 rooms: | [5 empty] | PASSIVE 1.5KW DSY3.aps | 002/1B2P/BED | 0 | PASSIVE 1.5KW DSY3.aps | 002/1B2P/BED | 0 | 0
[7 empty] | PASSIVE 1.5KW DSY3.aps | 003/3B5P/BED1 | 0 | PASSIVE 1.5KW DSY3.aps | 003/3B5P/BED1 | 0 | 0
Data: | [6 empty] | PASSIVE 1.5KW DSY3.aps | 003/3B5P/BED2 | 0 | PASSIVE 1.5KW DSY3.aps | 003/3B5P/BED2 | 0 | 0
Building category: | Category II (new builds.) | [5 empty] | PASSIVE 1.5KW DSY3.aps | 003/3B5P/BED3 | 0 | PASSIVE 1.5KW DSY3.aps | 003/3B5P/BED3 | 0 | 0
Weather file: | London_LWC_DSY3_2020High50.epw | [5 empty] | PASSIVE 1.5KW DSY3.aps | 004/3B5P/BED1 | 0 | PASSIVE 1.5KW DSY3.aps | 004/3B5P/BED1 | 0 | 0
Days data= | 365 | 2021-01-01 | 2021-12-31 |  |  |  | PASSIVE 1.5KW DSY3.aps | 004/3B5P/BED2 | 0 | PASSIVE 1.5KW DSY3.aps | 004/3B5P/BED2 | 0 | 0
Days (summer)= | 153 | 2021-05-01 | 2021-09-30 |  |  |  | PASSIVE 1.5KW DSY3.aps | 004/3B5P/BED3 | 0 | PASSIVE 1.5KW DSY3.aps | 004/3B5P/BED3 | 0 | 0
Data OK? | OK | Full summer |  |  |  |  | PASSIVE 1.5KW DSY3.aps | 005/3B5P/BED1 | 0 | PASSIVE 1.5KW DSY3.aps | 005/3B5P/BED1 | 0 | 0
[7 empty] | PASSIVE 1.5KW DSY3.aps | 005/3B5P/BED2 | 0 | PASSIVE 1.5KW DSY3.aps | 005/3B5P/BED2 | 0 | 0
Occupancy: | [6 empty] | PASSIVE 1.5KW DSY3.aps | 005/3B5P/BED3 | 0 | PASSIVE 1.5KW DSY3.aps | 005/3B5P/BED3 | 0 | 0
Note: | This report assesses occupied periods only. Please be aware that TM52 should be conducted for occupied and/or “available hours”. | [5 empty] | PASSIVE 1.5KW DSY3.aps | 006/3B5P/BED1 | 0 | PASSIVE 1.5KW DSY3.aps | 006/3B5P/BED1 | 0 | 0
| Use of educational NCM profiles may be seen as inappropriate due to prolonged unoccupied periods during summer months. | [5 empty] | PASSIVE 1.5KW DSY3.aps | 006/3B5P/BED2 | 0 | PASSIVE 1.5KW DSY3.aps | 006/3B5P/BED2 | 0 | 0
| See Section 6.1.2 (a) of TM52 for further information. | [5 empty] | PASSIVE 1.5KW DSY3.aps | 006/3B5P/BED3 | 0 | PASSIVE 1.5KW DSY3.aps | 006/3B5P/BED3 | 0 | 0
[7 empty] | PASSIVE 1.5KW DSY3.aps | 007/1B2P/BED | 0 | PASSIVE 1.5KW DSY3.aps | 007/1B2P/BED | 0 | 0
Passed: | 64 rooms: | [5 empty] | PASSIVE 1.5KW DSY3.aps | 008/1B2P/BED | 0 | PASSIVE 1.5KW DSY3.aps | 008/1B2P/BED | 0 | 0
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing | PASSIVE 1.5KW DSY3.aps | 009/4B6P/BED1 | 0 | PASSIVE 1.5KW DSY3.aps | 009/4B6P/BED1 | 0 | 0
001/1B2P/BED | 2 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 009/4B6P/BED2 | 0 | PASSIVE 1.5KW DSY3.aps | 009/4B6P/BED2 | 0 | 0
001/1B2P/LDK | 0 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 009/4B6P/BED3 | 0 | PASSIVE 1.5KW DSY3.aps | 009/4B6P/BED3 | 0 | 0
002/1B2P/BED | 7 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 009/4B6P/BED4 | 0 | PASSIVE 1.5KW DSY3.aps | 009/4B6P/BED4 | 0 | 0
002/1B2P/LDK | 5 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 010/4B6P/BED1 | 0 | PASSIVE 1.5KW DSY3.aps | 010/4B6P/BED1 | 0 | 0
003/3B5P/BED1 | 0000005A | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 010/4B6P/BED2 | 0 | PASSIVE 1.5KW DSY3.aps | 010/4B6P/BED2 | 0 | 0
003/3B5P/BED2 | 0000005B | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 010/4B6P/BED3 | 0 | PASSIVE 1.5KW DSY3.aps | 010/4B6P/BED3 | 0 | 0
003/3B5P/BED3 | 0000005C | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 010/4B6P/BED4 | 0 | PASSIVE 1.5KW DSY3.aps | 010/4B6P/BED4 | 0 | 0
003/3B5P/DINKIT | 0000000D | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 011/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY3.aps | 011/2B4P/BED1 | 0 | 0
003/3B5P/LIV | 0000000C | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 011/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY3.aps | 011/2B4P/BED2 | 0 | 0
004/3B5P/BED1 | 62 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 012/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY3.aps | 012/2B4P/BED1 | 0 | 0
004/3B5P/BED2 | 63 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 012/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY3.aps | 012/2B4P/BED2 | 0 | 0
004/3B5P/BED3 | 64 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 013/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY3.aps | 013/2B4P/BED1 | 0 | 0
004/3B5P/DINKIT | 19 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 013/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY3.aps | 013/2B4P/BED2 | 0 | 0
004/3B5P/LIV | 18 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 014/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY3.aps | 014/2B4P/BED1 | 0 | 0
005/3B5P/BED1 | 69 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 014/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY3.aps | 014/2B4P/BED2 | 0 | 0
005/3B5P/BED2 | 0000006A | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 015/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY3.aps | 015/2B4P/BED1 | 0 | 0
005/3B5P/BED3 | 0000006B | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 015/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY3.aps | 015/2B4P/BED2 | 0 | 0
005/3B5P/DINKIT | 0000001A | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 016/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY3.aps | 016/2B4P/BED1 | 0 | 0
005/3B5P/LIV | 0000001B | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 016/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY3.aps | 016/2B4P/BED2 | 0 | 0
006/3B5P/BED1 | 71 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 017/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY3.aps | 017/2B4P/BED1 | 0 | 0
006/3B5P/BED2 | 70 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 017/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY3.aps | 017/2B4P/BED2 | 0 | 0
006/3B5P/BED3 | 0000006F | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 018/2B4P/BED1 | 0 | PASSIVE 1.5KW DSY3.aps | 018/2B4P/BED1 | 0 | 0
006/3B5P/DINKIT | 27 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | 018/2B4P/BED2 | 0 | PASSIVE 1.5KW DSY3.aps | 018/2B4P/BED2 | 0 | 0
006/3B5P/LIV | 26 | 100 | 0 | 0 | 0 | - | PASSIVE 1.5KW DSY3.aps | Total hours | 0 | PASSIVE 1.5KW DSY3.aps | Total hours | 0
007/1B2P/BED | 29 | 100 | 0 | 0 | 0 | -
007/1B2P/LDK | 28 | 100 | 0 | 0 | 0 | -
008/1B2P/BED | 31 | 100 | 0 | 0 | 0 | -
008/1B2P/LDK | 30 | 100 | 0 | 0 | 0 | -
009/4B6P/BED1 | 76 | 100 | 0 | 0 | 0 | -
009/4B6P/BED2 | 77 | 100 | 0 | 0 | 0 | -
009/4B6P/BED3 | 78 | 100 | 0 | 0 | 0 | -
009/4B6P/BED4 | 79 | 100 | 0 | 0 | 0 | -
009/4B6P/DINKIT | 0000003D | 100 | 0 | 0 | 0 | -
009/4B6P/LIV | 0000003C | 100 | 0 | 0 | 0 | -
010/4B6P/BED1 | 1000026 | 100 | 0 | 0 | 0 | -
010/4B6P/BED2 | 1000027 | 100 | 0 | 0 | 0 | -
010/4B6P/BED3 | 1000028 | 100 | 0 | 0 | 0 | -
010/4B6P/BED4 | 1000029 | 100 | 0 | 0 | 0 | -
010/4B6P/DINKIT | 1000006 | 100 | 0 | 0 | 0 | -
010/4B6P/LIV | 1000005 | 100 | 0 | 0 | 0 | -
011/2B4P/BED1 | 1000009 | 100 | 0 | 0 | 0 | -
011/2B4P/BED2 | 0100000A | 100 | 0 | 0 | 0 | -
011/2B4P/LDK | 1000008 | 100 | 0 | 0 | 0 | -
012/2B4P/BED1 | 1000011 | 100 | 0 | 0 | 0 | -
012/2B4P/BED2 | 1000012 | 100 | 0 | 0 | 0 | -
012/2B4P/LDK | 1000010 | 100 | 0 | 0 | 0 | -
013/2B4P/BED1 | 1000017 | 100 | 0 | 0 | 0 | -
013/2B4P/BED2 | 1000018 | 100 | 0 | 0 | 0 | -
013/2B4P/LDK | 1000016 | 100 | 0 | 0 | 0 | -
014/2B4P/BED1 | 1000020 | 100 | 0 | 0 | 0 | -
014/2B4P/BED2 | 1000021 | 100 | 0 | 0 | 0 | -
014/2B4P/LDK | 0100001F | 100 | 0 | 0 | 0 | -
015/2B4P/BED1 | 0100002D | 100 | 0 | 0 | 0 | -
015/2B4P/BED2 | 0100002E | 100 | 0 | 0 | 0 | -
015/2B4P/LDK | 1000031 | 100 | 0 | 0 | 0 | -
016/2B4P/BED1 | 1000034 | 100 | 0 | 0 | 0 | -
016/2B4P/BED2 | 1000035 | 100 | 0 | 0 | 0 | -
016/2B4P/LDK | 1000038 | 100 | 0 | 0 | 0 | -
017/2B4P/BED1 | 0100003B | 100 | 0 | 0 | 0 | -
017/2B4P/BED2 | 0100003C | 100 | 0 | 0 | 0 | -
017/2B4P/LDK | 0100003A | 100 | 0 | 0 | 0 | -
018/2B4P/BED1 | 1000044 | 100 | 0 | 0 | 0 | -
018/2B4P/BED2 | 1000045 | 100 | 0 | 0 | 0 | -
018/2B4P/LDK | 1000043 | 100 | 0 | 0 | 0 | -
Failed: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Unoccupied: | 0 rooms:
Room Name | Room ID | Occupied days (%) | Criteria 1 (%Hrs Top-Tmax>=1K) | Criteria 2 (Max. Daily Deg.Hrs) | Criteria 3 (Max. DeltaT) | Criteria failing
Note: | A TM 52 2013 analysis provides an assessment of comfort compliance based on bulk air modelling
i.e. each space is considered idealised and the air in the space perfectly mixed. The assessment does
not assess placement of space features e.g. windows & openings, airflow patterns or discomfort issues.
The user should assess these design aspects outside of the TM52 analysis.